## Modbus-BACnet
ID | Variable | Description | DataType | Access | Modbus TCP/IP |  | Units | Special
[5 empty] | Variable Type | Variable index
2 | Cool_1.Val | IO - Digital Output - Cooler - Stage 1 [0 / 1] | BOOL | Read | Coil | 1 | 0 / 1 | 0 - ON 1 - OFF
3 | Cool_2.Val | IO - Digital Output - Cooler - Stage 2 [0 / 1] | BOOL | Read | Coil | 2 | 0 / 1 | 0 - ON 1 - OFF
4 | CoolAlrm.Val | IO - Digital Input - Cooler - Alarm [0 / 1] | BOOL | Read | Coil | 3 | 0 / 1
5 | CoolHeat.Val | IO - Digital Output - Heating - Signal [0 / 1] | BOOL | Read | Coil | 4 | 0 / 1 | 0 - ON 1 - OFF
7 | DoubleDamp.Val | IO - Digital Output - Damper - Redundant [0 / 1] | BOOL | Read | Coil | 5 | 0 / 1 | 0 - ON 1 - OFF
8 | ExhAirDamp.Val | IO - Digital Output - Damper - Supply [0 / 1] | BOOL | Read | Coil | 6 | 0 / 1 | 0 - ON 1 - OFF
13 | FireAlrm.Val | IO - Digital Input - Fire - Alarm [0 / 1] | BOOL | Read | Coil | 7 | 0 / 1
14 | Heat_1.Val | IO - Digital Output - Heater - Stage 1 [0 / 1] | BOOL | Read | Coil | 8 | 0 / 1 | 0 - ON 1 - OFF
15 | Heat_2.Val | IO - Digital Output - Heater - Stage 2 [0 / 1] | BOOL | Read | Coil | 9 | 0 / 1 | 0 - ON 1 - OFF
18 | Hum.Val | IO - Digital Output - Humidifier [0 / 1] | BOOL | Read | Coil | 10 | 0 / 1 | 0 - ON 1 - OFF
20 | HumAlrm.Val | IO - Digital Input - Humidifier - Alarm [0 / 1] | BOOL | Read | Coil | 11 | 0 / 1
21 | ID2_Alrm.Val | IO - Digital Input - Freeze - Alarm [0 / 1] | BOOL | Read | Coil | 12 | 0 / 1
40 | PreHeaterPump.Val | IO - Digital Output - PreHeater [0 / 1] | BOOL | Read | Coil | 13 | 0 / 1 | 0 - ON 1 - OFF
41 | RecoveryPump.Val | IO - Digital Output - Recovery [0 / 1] | BOOL | Read | Coil | 14 | 0 / 1 | 0 - ON 1 - OFF
43 | ReHeat.Val | IO - Digital Output - ReHeater [0 / 1] | BOOL | Read | Coil | 15 | 0 / 1 | 0 - ON 1 - OFF
45 | RemoteOn.Val | IO - Digital Input - Remote - ON [0 / 1] | BOOL | Read | Coil | 16 | 0 / 1
47 | RetFilter.Val | IO - Digital Input - Filter - Return [0 / 1] | BOOL | Read | Coil | 17 | 0 / 1
50 | SrsAlrm.Val | IO - Digital Output - Alarm - Global [0 / 1] | BOOL | Read | Coil | 18 | 0 / 1 | 0 - ON 1 - OFF
53 | SupplyFilter.Val | IO - Digital Input - Filter - Supply [0 / 1] | BOOL | Read | Coil | 19 | 0 / 1
59 | WinSum.Val | IO - Digital Input - Winter / Summer [0 / 1] | BOOL | Read | Coil | 20 | 0 / 1
63 | UnitCoolHeatMode | MO - Unit - Cooling / Heating [0 / 1] | BOOL | ReadWrite | Coil | 21 | 0 / 1 | 0 - Cooling 1 - Heating
135 | MixAirDamp_On | MO - Damper Mixing - On [0 / 1] | BOOL | Read | Coil | 22 | 0 / 1
143 | RunExhFan | MO - Fan - Return - On [0 / 1] | BOOL | Read | Coil | 23 | 0 / 1
144 | RunSupplyFan | MO - Fan - Supply - On [0 / 1] | BOOL | Read | Coil | 24 | 0 / 1
216 | UnitOff | MO - Unit - On [0 / 1] | BOOL | Read | Coil | 25 | 0 / 1
217 | UnitOn | MO - Unit - Off [0 / 1] | BOOL | Read | Coil | 26 | 0 / 1
283 | SchedOn | SCH - Scheduller - On [0 / 1] | BOOL | ReadWrite | Coil | 27 | 0 / 1 | 0 - OFF 1 - ON
286 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Enabled | SCH - Scheduller - Monday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 28 | 0 / 1 | 0 - OFF 1 - ON
287 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Flag_Enabled | SCH - Scheduller - Monday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 29 | 0 / 1
291 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Enabled | SCH - Scheduller - Monday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 30 | 0 / 1 | 0 - OFF 1 - ON
292 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Flag_Enabled | SCH - Scheduller - Monday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 31 | 0 / 1
296 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Enabled | SCH - Scheduller - Monday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 32 | 0 / 1 | 0 - OFF 1 - ON
297 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Flag_Enabled | SCH - Scheduller - Monday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 33 | 0 / 1
301 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Enabled | SCH - Scheduller - Monday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 34 | 0 / 1 | 0 - OFF 1 - ON
302 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Flag_Enabled | SCH - Scheduller - Monday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 35 | 0 / 1
306 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Enabled | SCH - Scheduller - Tuesday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 36 | 0 / 1 | 0 - OFF 1 - ON
307 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Flag_Enabled | SCH - Scheduller - Tuesday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 37 | 0 / 1
311 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Enabled | SCH - Scheduller - Tuesday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 38 | 0 / 1 | 0 - OFF 1 - ON
312 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Flag_Enabled | SCH - Scheduller - Tuesday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 39 | 0 / 1
316 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Enabled | SCH - Scheduller - Tuesday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 40 | 0 / 1 | 0 - OFF 1 - ON
317 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Flag_Enabled | SCH - Scheduller - Tuesday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 41 | 0 / 1
321 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Enabled | SCH - Scheduller - Tuesday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 42 | 0 / 1 | 0 - OFF 1 - ON
322 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Flag_Enabled | SCH - Scheduller - Tuesday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 43 | 0 / 1
326 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Enabled | SCH - Scheduller - Wednesday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 44 | 0 / 1 | 0 - OFF 1 - ON
327 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Flag_Enabled | SCH - Scheduller - Wednesday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 45 | 0 / 1
331 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Enabled | SCH - Scheduller - Wednesday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 46 | 0 / 1 | 0 - OFF 1 - ON
332 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Flag_Enabled | SCH - Scheduller - Wednesday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 47 | 0 / 1
336 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Enabled | SCH - Scheduller - Wednesday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 48 | 0 / 1 | 0 - OFF 1 - ON
337 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Flag_Enabled | SCH - Scheduller - Wednesday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 49 | 0 / 1
341 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Enabled | SCH - Scheduller - Wednesday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 50 | 0 / 1 | 0 - OFF 1 - ON
342 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Flag_Enabled | SCH - Scheduller - Wednesday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 51 | 0 / 1
346 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Enabled | SCH - Scheduller - Thursday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 52 | 0 / 1 | 0 - OFF 1 - ON
347 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Flag_Enabled | SCH - Scheduller - Thursday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 53 | 0 / 1
351 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Enabled | SCH - Scheduller - Thursday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 54 | 0 / 1 | 0 - OFF 1 - ON
352 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Flag_Enabled | SCH - Scheduller - Thursday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 55 | 0 / 1
356 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Enabled | SCH - Scheduller - Thursday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 56 | 0 / 1 | 0 - OFF 1 - ON
357 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Flag_Enabled | SCH - Scheduller - Thursday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 57 | 0 / 1
361 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Enabled | SCH - Scheduller - Thursday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 58 | 0 / 1 | 0 - OFF 1 - ON
362 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Flag_Enabled | SCH - Scheduller - Thursday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 59 | 0 / 1
366 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Enabled | SCH - Scheduller - Friday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 60 | 0 / 1 | 0 - OFF 1 - ON
367 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Flag_Enabled | SCH - Scheduller - Friday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 61 | 0 / 1
371 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Enabled | SCH - Scheduller - Friday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 62 | 0 / 1 | 0 - OFF 1 - ON
372 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Flag_Enabled | SCH - Scheduller - Friday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 63 | 0 / 1
376 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Enabled | SCH - Scheduller - Friday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 64 | 0 / 1 | 0 - OFF 1 - ON
377 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Flag_Enabled | SCH - Scheduller - Friday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 65 | 0 / 1
381 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Enabled | SCH - Scheduller - Friday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 66 | 0 / 1 | 0 - OFF 1 - ON
382 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Flag_Enabled | SCH - Scheduller - Friday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 67 | 0 / 1
386 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Enabled | SCH - Scheduller - Saturday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 68 | 0 / 1 | 0 - OFF 1 - ON
387 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Flag_Enabled | SCH - Scheduller - Saturday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 69 | 0 / 1
391 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Enabled | SCH - Scheduller - Saturday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 70 | 0 / 1 | 0 - OFF 1 - ON
392 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Flag_Enabled | SCH - Scheduller - Saturday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 71 | 0 / 1
396 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Enabled | SCH - Scheduller - Saturday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 72 | 0 / 1 | 0 - OFF 1 - ON
397 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Flag_Enabled | SCH - Scheduller - Saturday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 73 | 0 / 1
401 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Enabled | SCH - Scheduller - Saturday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 74 | 0 / 1 | 0 - OFF 1 - ON
402 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Flag_Enabled | SCH - Scheduller - Saturday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 75 | 0 / 1
406 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Enabled | SCH - Scheduller - Sunday - 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 76 | 0 / 1 | 0 - OFF 1 - ON
407 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Flag_Enabled | SCH - Scheduller - Sunday - 1 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 77 | 0 / 1
411 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Enabled | SCH - Scheduller - Sunday - 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 78 | 0 / 1 | 0 - OFF 1 - ON
412 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Flag_Enabled | SCH - Scheduller - Sunday - 2 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 79 | 0 / 1
416 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Enabled | SCH - Scheduller - Sunday - 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 80 | 0 / 1 | 0 - OFF 1 - ON
417 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Flag_Enabled | SCH - Scheduller - Sunday - 3 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 81 | 0 / 1
421 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Enabled | SCH - Scheduller - Sunday - 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 82 | 0 / 1 | 0 - OFF 1 - ON
422 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Flag_Enabled | SCH - Scheduller - Sunday - 4 - Flag_Enabled [0 / 1] | BOOL | ReadWrite | Coil | 83 | 0 / 1
428 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].Enabled | SCH - Scheduller - Special Days 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 84 | 0 / 1 | 0 - OFF 1 - ON
432 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].Enabled | SCH - Scheduller - Special Days 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 85 | 0 / 1 | 0 - OFF 1 - ON
436 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].Enabled | SCH - Scheduller - Special Days 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 86 | 0 / 1 | 0 - OFF 1 - ON
440 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].Enabled | SCH - Scheduller - Special Days 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 87 | 0 / 1 | 0 - OFF 1 - ON
444 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].Enabled | SCH - Scheduller - Special Days 5 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 88 | 0 / 1 | 0 - OFF 1 - ON
448 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].Enabled | SCH - Scheduller - Special Days 6 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 89 | 0 / 1 | 0 - OFF 1 - ON
452 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Enabled | SCH - Scheduller - Time Band 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 90 | 0 / 1 | 0 - OFF 1 - ON
456 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Enabled | SCH - Scheduller - Time Band 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 91 | 0 / 1 | 0 - OFF 1 - ON
460 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Enabled | SCH - Scheduller - Time Band 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 92 | 0 / 1 | 0 - OFF 1 - ON
464 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Enabled | SCH - Scheduller - Time Band 4 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 93 | 0 / 1 | 0 - OFF 1 - ON
468 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].Enabled | SCH - Scheduller - Periods 1 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 94 | 0 / 1 | 0 - OFF 1 - ON
474 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].Enabled | SCH - Scheduller - Periods 2 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 95 | 0 / 1 | 0 - OFF 1 - ON
480 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].Enabled | SCH - Scheduller - Periods 3 - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 96 | 0 / 1 | 0 - OFF 1 - ON
488 | SchedActive | SCH - Scheduller - Active [0 / 1] | BOOL | Read | Coil | 97 | 0 / 1 | 0 - NO 1 - YES
490 | Al_ABB_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 [0 / 1] | BOOL | Read | Coil | 98 | 0 / 1
491 | Al_ABB_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 [0 / 1] | BOOL | Read | Coil | 99 | 0 / 1
492 | Al_ABB_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 [0 / 1] | BOOL | Read | Coil | 100 | 0 / 1
493 | Al_ABB_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 [0 / 1] | BOOL | Read | Coil | 101 | 0 / 1
494 | Al_ABB_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 [0 / 1] | BOOL | Read | Coil | 102 | 0 / 1
495 | Al_ABB_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 [0 / 1] | BOOL | Read | Coil | 103 | 0 / 1
496 | Al_ABB_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 [0 / 1] | BOOL | Read | Coil | 104 | 0 / 1
497 | Al_ABB_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 [0 / 1] | BOOL | Read | Coil | 105 | 0 / 1
498 | Al_ABB_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 [0 / 1] | BOOL | Read | Coil | 106 | 0 / 1
499 | Al_ABB_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 [0 / 1] | BOOL | Read | Coil | 107 | 0 / 1
500 | Al_ABB_Rotary.Trigger | AL - Alarm - Rotary [0 / 1] | BOOL | Read | Coil | 108 | 0 / 1
501 | Al_ABB_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 [0 / 1] | BOOL | Read | Coil | 109 | 0 / 1
502 | Al_ABB_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 [0 / 1] | BOOL | Read | Coil | 110 | 0 / 1
503 | Al_ABB_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 [0 / 1] | BOOL | Read | Coil | 111 | 0 / 1
504 | Al_ABB_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 [0 / 1] | BOOL | Read | Coil | 112 | 0 / 1
505 | Al_ABB_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 [0 / 1] | BOOL | Read | Coil | 113 | 0 / 1
506 | Al_ABB_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 [0 / 1] | BOOL | Read | Coil | 114 | 0 / 1
507 | Al_ABB_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 [0 / 1] | BOOL | Read | Coil | 115 | 0 / 1
508 | Al_ABB_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 [0 / 1] | BOOL | Read | Coil | 116 | 0 / 1
509 | Al_ABB_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 [0 / 1] | BOOL | Read | Coil | 117 | 0 / 1
510 | Al_ABB_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 [0 / 1] | BOOL | Read | Coil | 118 | 0 / 1
511 | Al_AFreezeDIN.Trigger | AL - Alarm - Antifreeze - Digital Input [0 / 1] | BOOL | Read | Coil | 119 | 0 / 1
512 | Al_AFreezePRB.Trigger | AL - Alarm - Antifreeze - Back Water Temperature [0 / 1] | BOOL | Read | Coil | 120 | 0 / 1
513 | Al_AFreezePreHeatPRB.Trigger | AL - Alarm - Antifreeze - PreHeat Back Water Temperature [0 / 1] | BOOL | Read | Coil | 121 | 0 / 1
514 | Al_AfterPreHeatCoilTempPrb.Trigger | AL - Alarm - Probe - After preheating coil temperature [0 / 1] | BOOL | Read | Coil | 122 | 0 / 1
515 | Al_BMS_Offline.Trigger | AL - Alarm - BMS - Offline [0 / 1] | BOOL | Read | Coil | 123 | 0 / 1
516 | Al_CfgError_cpCOe.Trigger | AL - Alarm - Module IO - cPCOE - Configuration error [0 / 1] | BOOL | Read | Coil | 124 | 0 / 1
517 | Al_CircuitFault_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 125 | 0 / 1
518 | Al_CircuitFault_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 126 | 0 / 1
519 | Al_CircuitFault_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 127 | 0 / 1
520 | Al_CircuitFault_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 128 | 0 / 1
521 | Al_CircuitFault_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 129 | 0 / 1
522 | Al_CircuitFault_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 130 | 0 / 1
523 | Al_CircuitFault_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 131 | 0 / 1
524 | Al_CircuitFault_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 132 | 0 / 1
525 | Al_CircuitFault_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 133 | 0 / 1
526 | Al_CircuitFault_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 134 | 0 / 1
527 | Al_CircuitFault_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 135 | 0 / 1
528 | Al_CircuitFault_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 136 | 0 / 1
529 | Al_CircuitFault_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 137 | 0 / 1
530 | Al_CircuitFault_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 138 | 0 / 1
531 | Al_CircuitFault_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 139 | 0 / 1
532 | Al_CircuitFault_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 140 | 0 / 1
533 | Al_CircuitFault_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 141 | 0 / 1
534 | Al_CircuitFault_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 142 | 0 / 1
535 | Al_CircuitFault_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 143 | 0 / 1
536 | Al_CircuitFault_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 144 | 0 / 1
537 | Al_CommErr_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Communication Error [0 / 1] | BOOL | Read | Coil | 145 | 0 / 1
538 | Al_CommErr_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Communication Error [0 / 1] | BOOL | Read | Coil | 146 | 0 / 1
539 | Al_CommErr_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Communication Error [0 / 1] | BOOL | Read | Coil | 147 | 0 / 1
540 | Al_CommErr_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Communication Error [0 / 1] | BOOL | Read | Coil | 148 | 0 / 1
541 | Al_CommErr_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Communication Error [0 / 1] | BOOL | Read | Coil | 149 | 0 / 1
542 | Al_CommErr_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Communication Error [0 / 1] | BOOL | Read | Coil | 150 | 0 / 1
543 | Al_CommErr_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Communication Error [0 / 1] | BOOL | Read | Coil | 151 | 0 / 1
544 | Al_CommErr_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Communication Error [0 / 1] | BOOL | Read | Coil | 152 | 0 / 1
545 | Al_CommErr_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Communication Error [0 / 1] | BOOL | Read | Coil | 153 | 0 / 1
546 | Al_CommErr_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Communication Error [0 / 1] | BOOL | Read | Coil | 154 | 0 / 1
547 | Al_CommErr_Rotary.Trigger | AL - Alarm - Rotary - CommUnitation Error [0 / 1] | BOOL | Read | Coil | 155 | 0 / 1
548 | Al_CommErr_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Communication Error [0 / 1] | BOOL | Read | Coil | 156 | 0 / 1
549 | Al_CommErr_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Communication Error [0 / 1] | BOOL | Read | Coil | 157 | 0 / 1
550 | Al_CommErr_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Communication Error [0 / 1] | BOOL | Read | Coil | 158 | 0 / 1
551 | Al_CommErr_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Communication Error [0 / 1] | BOOL | Read | Coil | 159 | 0 / 1
552 | Al_CommErr_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Communication Error [0 / 1] | BOOL | Read | Coil | 160 | 0 / 1
553 | Al_CommErr_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Communication Error [0 / 1] | BOOL | Read | Coil | 161 | 0 / 1
554 | Al_CommErr_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Communication Error [0 / 1] | BOOL | Read | Coil | 162 | 0 / 1
555 | Al_CommErr_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Communication Error [0 / 1] | BOOL | Read | Coil | 163 | 0 / 1
556 | Al_CommErr_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Communication Error [0 / 1] | BOOL | Read | Coil | 164 | 0 / 1
557 | Al_CommErr_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Communication Error [0 / 1] | BOOL | Read | Coil | 165 | 0 / 1
558 | Al_Cool.Trigger | AL - Alarm - Cooling - Device Alarm [0 / 1] | BOOL | Read | Coil | 166 | 0 / 1
559 | Al_CoolFanFault_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 167 | 0 / 1
560 | Al_CoolFanFault_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 168 | 0 / 1
561 | Al_CoolFanFault_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 169 | 0 / 1
562 | Al_CoolFanFault_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 170 | 0 / 1
563 | Al_CoolFanFault_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 171 | 0 / 1
564 | Al_CoolFanFault_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 172 | 0 / 1
565 | Al_CoolFanFault_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 173 | 0 / 1
566 | Al_CoolFanFault_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 174 | 0 / 1
567 | Al_CoolFanFault_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 175 | 0 / 1
568 | Al_CoolFanFault_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 176 | 0 / 1
569 | Al_CoolFanFault_Rotary.Trigger | AL - Alarm - Rotary - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 177 | 0 / 1
570 | Al_CoolFanFault_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 178 | 0 / 1
571 | Al_CoolFanFault_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 179 | 0 / 1
572 | Al_CoolFanFault_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 180 | 0 / 1
573 | Al_CoolFanFault_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 181 | 0 / 1
574 | Al_CoolFanFault_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 182 | 0 / 1
575 | Al_CoolFanFault_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 183 | 0 / 1
576 | Al_CoolFanFault_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 184 | 0 / 1
577 | Al_CoolFanFault_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 185 | 0 / 1
578 | Al_CoolFanFault_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 186 | 0 / 1
579 | Al_CoolFanFault_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 187 | 0 / 1
580 | Al_CutOff_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - CutOff [0 / 1] | BOOL | Read | Coil | 188 | 0 / 1
581 | Al_CutOff_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - CutOff [0 / 1] | BOOL | Read | Coil | 189 | 0 / 1
582 | Al_CutOff_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - CutOff [0 / 1] | BOOL | Read | Coil | 190 | 0 / 1
583 | Al_CutOff_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - CutOff [0 / 1] | BOOL | Read | Coil | 191 | 0 / 1
584 | Al_CutOff_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - CutOff [0 / 1] | BOOL | Read | Coil | 192 | 0 / 1
585 | Al_CutOff_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - CutOff [0 / 1] | BOOL | Read | Coil | 193 | 0 / 1
586 | Al_CutOff_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - CutOff [0 / 1] | BOOL | Read | Coil | 194 | 0 / 1
587 | Al_CutOff_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - CutOff [0 / 1] | BOOL | Read | Coil | 195 | 0 / 1
588 | Al_CutOff_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - CutOff [0 / 1] | BOOL | Read | Coil | 196 | 0 / 1
589 | Al_CutOff_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - CutOff [0 / 1] | BOOL | Read | Coil | 197 | 0 / 1
590 | Al_CutOff_Rotary.Trigger | AL - Alarm - Rotary - CutOff [0 / 1] | BOOL | Read | Coil | 198 | 0 / 1
591 | Al_CutOff_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - CutOff [0 / 1] | BOOL | Read | Coil | 199 | 0 / 1
592 | Al_CutOff_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - CutOff [0 / 1] | BOOL | Read | Coil | 200 | 0 / 1
593 | Al_CutOff_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - CutOff [0 / 1] | BOOL | Read | Coil | 201 | 0 / 1
594 | Al_CutOff_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - CutOff [0 / 1] | BOOL | Read | Coil | 202 | 0 / 1
595 | Al_CutOff_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - CutOff [0 / 1] | BOOL | Read | Coil | 203 | 0 / 1
596 | Al_CutOff_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - CutOff [0 / 1] | BOOL | Read | Coil | 204 | 0 / 1
597 | Al_CutOff_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - CutOff [0 / 1] | BOOL | Read | Coil | 205 | 0 / 1
598 | Al_CutOff_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - CutOff [0 / 1] | BOOL | Read | Coil | 206 | 0 / 1
599 | Al_CutOff_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - CutOff [0 / 1] | BOOL | Read | Coil | 207 | 0 / 1
600 | Al_CutOff_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - CutOff [0 / 1] | BOOL | Read | Coil | 208 | 0 / 1
601 | Al_DC_Ovld_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - DC Over load [0 / 1] | BOOL | Read | Coil | 209 | 0 / 1
602 | Al_DC_Ovld_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - DC Over load [0 / 1] | BOOL | Read | Coil | 210 | 0 / 1
603 | Al_DC_Ovld_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - DC Over load [0 / 1] | BOOL | Read | Coil | 211 | 0 / 1
604 | Al_DC_Ovld_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - DC Over load [0 / 1] | BOOL | Read | Coil | 212 | 0 / 1
605 | Al_DC_Ovld_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - DC Over load [0 / 1] | BOOL | Read | Coil | 213 | 0 / 1
606 | Al_DC_Ovld_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - DC Over load [0 / 1] | BOOL | Read | Coil | 214 | 0 / 1
607 | Al_DC_Ovld_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - DC Over load [0 / 1] | BOOL | Read | Coil | 215 | 0 / 1
608 | Al_DC_Ovld_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - DC Over load [0 / 1] | BOOL | Read | Coil | 216 | 0 / 1
609 | Al_DC_Ovld_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - DC Over load [0 / 1] | BOOL | Read | Coil | 217 | 0 / 1
610 | Al_DC_Ovld_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - DC Over load [0 / 1] | BOOL | Read | Coil | 218 | 0 / 1
611 | Al_DC_Ovld_Rotary.Trigger | AL - Alarm - Rotary - DC Overload [0 / 1] | BOOL | Read | Coil | 219 | 0 / 1
612 | Al_DC_Ovld_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - DC Over load [0 / 1] | BOOL | Read | Coil | 220 | 0 / 1
613 | Al_DC_Ovld_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - DC Over load [0 / 1] | BOOL | Read | Coil | 221 | 0 / 1
614 | Al_DC_Ovld_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - DC Over load [0 / 1] | BOOL | Read | Coil | 222 | 0 / 1
615 | Al_DC_Ovld_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - DC Over load [0 / 1] | BOOL | Read | Coil | 223 | 0 / 1
616 | Al_DC_Ovld_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - DC Over load [0 / 1] | BOOL | Read | Coil | 224 | 0 / 1
617 | Al_DC_Ovld_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - DC Over load [0 / 1] | BOOL | Read | Coil | 225 | 0 / 1
618 | Al_DC_Ovld_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - DC Over load [0 / 1] | BOOL | Read | Coil | 226 | 0 / 1
619 | Al_DC_Ovld_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - DC Over load [0 / 1] | BOOL | Read | Coil | 227 | 0 / 1
620 | Al_DC_Ovld_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - DC Over load [0 / 1] | BOOL | Read | Coil | 228 | 0 / 1
621 | Al_DC_Ovld_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - DC Over load [0 / 1] | BOOL | Read | Coil | 229 | 0 / 1
622 | Al_ElectTherm_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 230 | 0 / 1
623 | Al_ElectTherm_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 231 | 0 / 1
624 | Al_ElectTherm_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 232 | 0 / 1
625 | Al_ElectTherm_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 233 | 0 / 1
626 | Al_ElectTherm_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 234 | 0 / 1
627 | Al_ElectTherm_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 235 | 0 / 1
628 | Al_ElectTherm_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 236 | 0 / 1
629 | Al_ElectTherm_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 237 | 0 / 1
630 | Al_ElectTherm_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 238 | 0 / 1
631 | Al_ElectTherm_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 239 | 0 / 1
632 | Al_ElectTherm_Rotary.Trigger | AL - Alarm - Rotary - Electric Thermal [0 / 1] | BOOL | Read | Coil | 240 | 0 / 1
633 | Al_ElectTherm_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 241 | 0 / 1
634 | Al_ElectTherm_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 242 | 0 / 1
635 | Al_ElectTherm_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 243 | 0 / 1
636 | Al_ElectTherm_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 244 | 0 / 1
637 | Al_ElectTherm_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 245 | 0 / 1
638 | Al_ElectTherm_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 246 | 0 / 1
639 | Al_ElectTherm_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 247 | 0 / 1
640 | Al_ElectTherm_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 248 | 0 / 1
641 | Al_ElectTherm_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 249 | 0 / 1
642 | Al_ElectTherm_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 250 | 0 / 1
643 | Al_Err_retain_write.Trigger | AL - Alarm - Error retain write [0 / 1] | BOOL | Read | Coil | 251 | 0 / 1
644 | Al_ExhTempPrb.Trigger | AL - Alarm - Probe - Temperature Exhaust [0 / 1] | BOOL | Read | Coil | 252 | 0 / 1
645 | Al_ExtFaultA_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - External Fault A [0 / 1] | BOOL | Read | Coil | 253 | 0 / 1
646 | Al_ExtFaultA_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - External Fault A [0 / 1] | BOOL | Read | Coil | 254 | 0 / 1
647 | Al_ExtFaultA_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - External Fault A [0 / 1] | BOOL | Read | Coil | 255 | 0 / 1
648 | Al_ExtFaultA_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - External Fault A [0 / 1] | BOOL | Read | Coil | 256 | 0 / 1
649 | Al_ExtFaultA_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - External Fault A [0 / 1] | BOOL | Read | Coil | 257 | 0 / 1
650 | Al_ExtFaultA_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - External Fault A [0 / 1] | BOOL | Read | Coil | 258 | 0 / 1
651 | Al_ExtFaultA_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - External Fault A [0 / 1] | BOOL | Read | Coil | 259 | 0 / 1
652 | Al_ExtFaultA_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - External Fault A [0 / 1] | BOOL | Read | Coil | 260 | 0 / 1
653 | Al_ExtFaultA_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - External Fault A [0 / 1] | BOOL | Read | Coil | 261 | 0 / 1
654 | Al_ExtFaultA_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - External Fault A [0 / 1] | BOOL | Read | Coil | 262 | 0 / 1
655 | Al_ExtFaultA_Rotary.Trigger | AL - Alarm - Rotary - External Fault A [0 / 1] | BOOL | Read | Coil | 263 | 0 / 1
656 | Al_ExtFaultA_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - External Fault A [0 / 1] | BOOL | Read | Coil | 264 | 0 / 1
657 | Al_ExtFaultA_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - External Fault A [0 / 1] | BOOL | Read | Coil | 265 | 0 / 1
658 | Al_ExtFaultA_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - External Fault A [0 / 1] | BOOL | Read | Coil | 266 | 0 / 1
659 | Al_ExtFaultA_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - External Fault A [0 / 1] | BOOL | Read | Coil | 267 | 0 / 1
660 | Al_ExtFaultA_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - External Fault A [0 / 1] | BOOL | Read | Coil | 268 | 0 / 1
661 | Al_ExtFaultA_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - External Fault A [0 / 1] | BOOL | Read | Coil | 269 | 0 / 1
662 | Al_ExtFaultA_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - External Fault A [0 / 1] | BOOL | Read | Coil | 270 | 0 / 1
663 | Al_ExtFaultA_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - External Fault A [0 / 1] | BOOL | Read | Coil | 271 | 0 / 1
664 | Al_ExtFaultA_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - External Fault A [0 / 1] | BOOL | Read | Coil | 272 | 0 / 1
665 | Al_ExtFaultA_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - External Fault A [0 / 1] | BOOL | Read | Coil | 273 | 0 / 1
666 | Al_ExtFaultB_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - External Fault B [0 / 1] | BOOL | Read | Coil | 274 | 0 / 1
667 | Al_ExtFaultB_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - External Fault B [0 / 1] | BOOL | Read | Coil | 275 | 0 / 1
668 | Al_ExtFaultB_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - External Fault B [0 / 1] | BOOL | Read | Coil | 276 | 0 / 1
669 | Al_ExtFaultB_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - External Fault B [0 / 1] | BOOL | Read | Coil | 277 | 0 / 1
670 | Al_ExtFaultB_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - External Fault B [0 / 1] | BOOL | Read | Coil | 278 | 0 / 1
671 | Al_ExtFaultB_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - External Fault B [0 / 1] | BOOL | Read | Coil | 279 | 0 / 1
672 | Al_ExtFaultB_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - External Fault B [0 / 1] | BOOL | Read | Coil | 280 | 0 / 1
673 | Al_ExtFaultB_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - External Fault B [0 / 1] | BOOL | Read | Coil | 281 | 0 / 1
674 | Al_ExtFaultB_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - External Fault B [0 / 1] | BOOL | Read | Coil | 282 | 0 / 1
675 | Al_ExtFaultB_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - External Fault B [0 / 1] | BOOL | Read | Coil | 283 | 0 / 1
676 | Al_ExtFaultB_Rotary.Trigger | AL - Alarm - Rotary - External Fault B [0 / 1] | BOOL | Read | Coil | 284 | 0 / 1
677 | Al_ExtFaultB_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - External Fault B [0 / 1] | BOOL | Read | Coil | 285 | 0 / 1
678 | Al_ExtFaultB_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - External Fault B [0 / 1] | BOOL | Read | Coil | 286 | 0 / 1
679 | Al_ExtFaultB_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - External Fault B [0 / 1] | BOOL | Read | Coil | 287 | 0 / 1
680 | Al_ExtFaultB_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - External Fault B [0 / 1] | BOOL | Read | Coil | 288 | 0 / 1
681 | Al_ExtFaultB_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - External Fault B [0 / 1] | BOOL | Read | Coil | 289 | 0 / 1
682 | Al_ExtFaultB_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - External Fault B [0 / 1] | BOOL | Read | Coil | 290 | 0 / 1
683 | Al_ExtFaultB_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - External Fault B [0 / 1] | BOOL | Read | Coil | 291 | 0 / 1
684 | Al_ExtFaultB_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - External Fault B [0 / 1] | BOOL | Read | Coil | 292 | 0 / 1
685 | Al_ExtFaultB_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - External Fault B [0 / 1] | BOOL | Read | Coil | 293 | 0 / 1
686 | Al_ExtFaultB_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - External Fault B [0 / 1] | BOOL | Read | Coil | 294 | 0 / 1
687 | Al_ExtTempPrb.Trigger | AL - Alarm - Probe - Temperature External [0 / 1] | BOOL | Read | Coil | 295 | 0 / 1
688 | Al_Fire.Trigger | AL - Alarm - Fire [0 / 1] | BOOL | Read | Coil | 296 | 0 / 1
689 | Al_FireExh.Trigger | AL - Alarm - Fire - Return Temperature [0 / 1] | BOOL | Read | Coil | 297 | 0 / 1
690 | Al_GroundFault_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Ground Fault [0 / 1] | BOOL | Read | Coil | 298 | 0 / 1
691 | Al_GroundFault_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Ground Fault [0 / 1] | BOOL | Read | Coil | 299 | 0 / 1
692 | Al_GroundFault_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Ground Fault [0 / 1] | BOOL | Read | Coil | 300 | 0 / 1
693 | Al_GroundFault_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Ground Fault [0 / 1] | BOOL | Read | Coil | 301 | 0 / 1
694 | Al_GroundFault_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Ground Fault [0 / 1] | BOOL | Read | Coil | 302 | 0 / 1
695 | Al_GroundFault_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Ground Fault [0 / 1] | BOOL | Read | Coil | 303 | 0 / 1
696 | Al_GroundFault_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Ground Fault [0 / 1] | BOOL | Read | Coil | 304 | 0 / 1
697 | Al_GroundFault_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Ground Fault [0 / 1] | BOOL | Read | Coil | 305 | 0 / 1
698 | Al_GroundFault_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Ground Fault [0 / 1] | BOOL | Read | Coil | 306 | 0 / 1
699 | Al_GroundFault_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Ground Fault [0 / 1] | BOOL | Read | Coil | 307 | 0 / 1
700 | Al_GroundFault_Rotary.Trigger | AL - Alarm - Rotary - Ground Fault [0 / 1] | BOOL | Read | Coil | 308 | 0 / 1
701 | Al_GroundFault_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Ground Fault [0 / 1] | BOOL | Read | Coil | 309 | 0 / 1
702 | Al_GroundFault_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Ground Fault [0 / 1] | BOOL | Read | Coil | 310 | 0 / 1
703 | Al_GroundFault_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Ground Fault [0 / 1] | BOOL | Read | Coil | 311 | 0 / 1
704 | Al_GroundFault_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Ground Fault [0 / 1] | BOOL | Read | Coil | 312 | 0 / 1
705 | Al_GroundFault_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Ground Fault [0 / 1] | BOOL | Read | Coil | 313 | 0 / 1
706 | Al_GroundFault_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Ground Fault [0 / 1] | BOOL | Read | Coil | 314 | 0 / 1
707 | Al_GroundFault_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Ground Fault [0 / 1] | BOOL | Read | Coil | 315 | 0 / 1
708 | Al_GroundFault_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Ground Fault [0 / 1] | BOOL | Read | Coil | 316 | 0 / 1
709 | Al_GroundFault_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Ground Fault [0 / 1] | BOOL | Read | Coil | 317 | 0 / 1
710 | Al_GroundFault_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Ground Fault [0 / 1] | BOOL | Read | Coil | 318 | 0 / 1
711 | Al_Heat.Trigger | AL - Alarm - Heating - Device Alarm [0 / 1] | BOOL | Read | Coil | 319 | 0 / 1
712 | Al_HeatCoilTempPrb.Trigger | AL - Alarm - Probe - Temperature Water Heating coil [0 / 1] | BOOL | Read | Coil | 320 | 0 / 1
713 | Al_HeatExchgWorkHrsWarn.Trigger | AL - Alarm - HeatExchanger - HeatExchanger Works Hour Warning [0 / 1] | BOOL | Read | Coil | 321 | 0 / 1
714 | Al_HeatSink_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - HeatSink [0 / 1] | BOOL | Read | Coil | 322 | 0 / 1
715 | Al_HeatSink_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - HeatSink [0 / 1] | BOOL | Read | Coil | 323 | 0 / 1
716 | Al_HeatSink_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - HeatSink [0 / 1] | BOOL | Read | Coil | 324 | 0 / 1
717 | Al_HeatSink_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - HeatSink [0 / 1] | BOOL | Read | Coil | 325 | 0 / 1
718 | Al_HeatSink_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - HeatSink [0 / 1] | BOOL | Read | Coil | 326 | 0 / 1
719 | Al_HeatSink_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - HeatSink [0 / 1] | BOOL | Read | Coil | 327 | 0 / 1
720 | Al_HeatSink_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - HeatSink [0 / 1] | BOOL | Read | Coil | 328 | 0 / 1
721 | Al_HeatSink_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - HeatSink [0 / 1] | BOOL | Read | Coil | 329 | 0 / 1
722 | Al_HeatSink_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - HeatSink [0 / 1] | BOOL | Read | Coil | 330 | 0 / 1
723 | Al_HeatSink_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - HeatSink [0 / 1] | BOOL | Read | Coil | 331 | 0 / 1
724 | Al_HeatSink_Rotary.Trigger | AL - Alarm - Rotary - HeatSink [0 / 1] | BOOL | Read | Coil | 332 | 0 / 1
725 | Al_HeatSink_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - HeatSink [0 / 1] | BOOL | Read | Coil | 333 | 0 / 1
726 | Al_HeatSink_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - HeatSink [0 / 1] | BOOL | Read | Coil | 334 | 0 / 1
727 | Al_HeatSink_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - HeatSink [0 / 1] | BOOL | Read | Coil | 335 | 0 / 1
728 | Al_HeatSink_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - HeatSink [0 / 1] | BOOL | Read | Coil | 336 | 0 / 1
729 | Al_HeatSink_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - HeatSink [0 / 1] | BOOL | Read | Coil | 337 | 0 / 1
730 | Al_HeatSink_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - HeatSink [0 / 1] | BOOL | Read | Coil | 338 | 0 / 1
731 | Al_HeatSink_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - HeatSink [0 / 1] | BOOL | Read | Coil | 339 | 0 / 1
732 | Al_HeatSink_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - HeatSink [0 / 1] | BOOL | Read | Coil | 340 | 0 / 1
733 | Al_HeatSink_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - HeatSink [0 / 1] | BOOL | Read | Coil | 341 | 0 / 1
734 | Al_HeatSink_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - HeatSink [0 / 1] | BOOL | Read | Coil | 342 | 0 / 1
735 | AL_Hot_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Hot [0 / 1] | BOOL | Read | Coil | 343 | 0 / 1
736 | AL_Hot_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Hot [0 / 1] | BOOL | Read | Coil | 344 | 0 / 1
737 | AL_Hot_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Hot [0 / 1] | BOOL | Read | Coil | 345 | 0 / 1
738 | AL_Hot_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Hot [0 / 1] | BOOL | Read | Coil | 346 | 0 / 1
739 | AL_Hot_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Hot [0 / 1] | BOOL | Read | Coil | 347 | 0 / 1
740 | AL_Hot_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Hot [0 / 1] | BOOL | Read | Coil | 348 | 0 / 1
741 | AL_Hot_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Hot [0 / 1] | BOOL | Read | Coil | 349 | 0 / 1
742 | AL_Hot_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Hot [0 / 1] | BOOL | Read | Coil | 350 | 0 / 1
743 | AL_Hot_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Hot [0 / 1] | BOOL | Read | Coil | 351 | 0 / 1
744 | AL_Hot_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Hot [0 / 1] | BOOL | Read | Coil | 352 | 0 / 1
745 | AL_Hot_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Hot [0 / 1] | BOOL | Read | Coil | 353 | 0 / 1
746 | AL_Hot_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Hot [0 / 1] | BOOL | Read | Coil | 354 | 0 / 1
747 | AL_Hot_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Hot [0 / 1] | BOOL | Read | Coil | 355 | 0 / 1
748 | AL_Hot_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Hot [0 / 1] | BOOL | Read | Coil | 356 | 0 / 1
749 | AL_Hot_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Hot [0 / 1] | BOOL | Read | Coil | 357 | 0 / 1
750 | AL_Hot_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Hot [0 / 1] | BOOL | Read | Coil | 358 | 0 / 1
751 | AL_Hot_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Hot [0 / 1] | BOOL | Read | Coil | 359 | 0 / 1
752 | AL_Hot_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Hot [0 / 1] | BOOL | Read | Coil | 360 | 0 / 1
753 | AL_Hot_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Hot [0 / 1] | BOOL | Read | Coil | 361 | 0 / 1
754 | AL_Hot_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Hot [0 / 1] | BOOL | Read | Coil | 362 | 0 / 1
755 | Al_Hum.Trigger | AL - Alarm - Humidifier [0 / 1] | BOOL | Read | Coil | 363 | 0 / 1
756 | Al_HumWorkHrsWarn.Trigger | AL - Alarm - Humidity - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 364 | 0 / 1
757 | Al_HW_Fault_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 365 | 0 / 1
758 | Al_HW_Fault_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 366 | 0 / 1
759 | Al_HW_Fault_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 367 | 0 / 1
760 | Al_HW_Fault_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 368 | 0 / 1
761 | Al_HW_Fault_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 369 | 0 / 1
762 | Al_HW_Fault_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 370 | 0 / 1
763 | Al_HW_Fault_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 371 | 0 / 1
764 | Al_HW_Fault_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 372 | 0 / 1
765 | Al_HW_Fault_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 373 | 0 / 1
766 | Al_HW_Fault_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 374 | 0 / 1
767 | Al_HW_Fault_Rotary.Trigger | AL - Alarm - Rotary - Hardware Fault [0 / 1] | BOOL | Read | Coil | 375 | 0 / 1
768 | Al_HW_Fault_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 376 | 0 / 1
769 | Al_HW_Fault_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 377 | 0 / 1
770 | Al_HW_Fault_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 378 | 0 / 1
771 | Al_HW_Fault_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 379 | 0 / 1
772 | Al_HW_Fault_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 380 | 0 / 1
773 | Al_HW_Fault_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 381 | 0 / 1
774 | Al_HW_Fault_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 382 | 0 / 1
775 | Al_HW_Fault_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 383 | 0 / 1
776 | Al_HW_Fault_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 384 | 0 / 1
777 | Al_HW_Fault_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 385 | 0 / 1
778 | Al_I2RIGBTFault_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 386 | 0 / 1
779 | Al_I2RIGBTFault_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 387 | 0 / 1
780 | Al_I2RIGBTFault_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 388 | 0 / 1
781 | Al_I2RIGBTFault_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 389 | 0 / 1
782 | Al_I2RIGBTFault_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 390 | 0 / 1
783 | Al_I2RIGBTFault_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 391 | 0 / 1
784 | Al_I2RIGBTFault_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 392 | 0 / 1
785 | Al_I2RIGBTFault_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 393 | 0 / 1
786 | Al_I2RIGBTFault_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 394 | 0 / 1
787 | Al_I2RIGBTFault_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 395 | 0 / 1
788 | Al_I2RIGBTFault_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 396 | 0 / 1
789 | Al_I2RIGBTFault_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 397 | 0 / 1
790 | Al_I2RIGBTFault_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 398 | 0 / 1
791 | Al_I2RIGBTFault_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 399 | 0 / 1
792 | Al_I2RIGBTFault_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 400 | 0 / 1
793 | Al_I2RIGBTFault_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 401 | 0 / 1
794 | Al_I2RIGBTFault_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 402 | 0 / 1
795 | Al_I2RIGBTFault_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 403 | 0 / 1
796 | Al_I2RIGBTFault_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 404 | 0 / 1
797 | Al_I2RIGBTFault_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 405 | 0 / 1
798 | AL_IGBTOvercurrent_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 406 | 0 / 1
799 | AL_IGBTOvercurrent_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 407 | 0 / 1
800 | AL_IGBTOvercurrent_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 408 | 0 / 1
801 | AL_IGBTOvercurrent_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 409 | 0 / 1
802 | AL_IGBTOvercurrent_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 410 | 0 / 1
803 | AL_IGBTOvercurrent_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 411 | 0 / 1
804 | AL_IGBTOvercurrent_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 412 | 0 / 1
805 | AL_IGBTOvercurrent_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 413 | 0 / 1
806 | AL_IGBTOvercurrent_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 414 | 0 / 1
807 | AL_IGBTOvercurrent_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 415 | 0 / 1
808 | AL_IGBTOvercurrent_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 416 | 0 / 1
809 | AL_IGBTOvercurrent_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 417 | 0 / 1
810 | AL_IGBTOvercurrent_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 418 | 0 / 1
811 | AL_IGBTOvercurrent_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 419 | 0 / 1
812 | AL_IGBTOvercurrent_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 420 | 0 / 1
813 | AL_IGBTOvercurrent_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 421 | 0 / 1
814 | AL_IGBTOvercurrent_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 422 | 0 / 1
815 | AL_IGBTOvercurrent_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 423 | 0 / 1
816 | AL_IGBTOvercurrent_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 424 | 0 / 1
817 | AL_IGBTOvercurrent_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 425 | 0 / 1
818 | Al_InvOverheat_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 426 | 0 / 1
819 | Al_InvOverheat_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 427 | 0 / 1
820 | Al_InvOverheat_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 428 | 0 / 1
821 | Al_InvOverheat_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 429 | 0 / 1
822 | Al_InvOverheat_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 430 | 0 / 1
823 | Al_InvOverheat_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 431 | 0 / 1
824 | Al_InvOverheat_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 432 | 0 / 1
825 | Al_InvOverheat_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 433 | 0 / 1
826 | Al_InvOverheat_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 434 | 0 / 1
827 | Al_InvOverheat_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 435 | 0 / 1
828 | Al_InvOverheat_Rotary.Trigger | AL - Alarm - Rotary - Inverter OverHeat [0 / 1] | BOOL | Read | Coil | 436 | 0 / 1
829 | Al_InvOverheat_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 437 | 0 / 1
830 | Al_InvOverheat_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 438 | 0 / 1
831 | Al_InvOverheat_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 439 | 0 / 1
832 | Al_InvOverheat_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 440 | 0 / 1
833 | Al_InvOverheat_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 441 | 0 / 1
834 | Al_InvOverheat_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 442 | 0 / 1
835 | Al_InvOverheat_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 443 | 0 / 1
836 | Al_InvOverheat_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 444 | 0 / 1
837 | Al_InvOverheat_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 445 | 0 / 1
838 | Al_InvOverheat_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 446 | 0 / 1
839 | Al_InvOvld_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 447 | 0 / 1
840 | Al_InvOvld_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 448 | 0 / 1
841 | Al_InvOvld_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 449 | 0 / 1
842 | Al_InvOvld_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 450 | 0 / 1
843 | Al_InvOvld_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 451 | 0 / 1
844 | Al_InvOvld_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 452 | 0 / 1
845 | Al_InvOvld_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 453 | 0 / 1
846 | Al_InvOvld_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 454 | 0 / 1
847 | Al_InvOvld_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 455 | 0 / 1
848 | Al_InvOvld_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 456 | 0 / 1
849 | Al_InvOvld_Rotary.Trigger | AL - Alarm - Rotary - Inverter OverLoad [0 / 1] | BOOL | Read | Coil | 457 | 0 / 1
850 | Al_InvOvld_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 458 | 0 / 1
851 | Al_InvOvld_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 459 | 0 / 1
852 | Al_InvOvld_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 460 | 0 / 1
853 | Al_InvOvld_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 461 | 0 / 1
854 | Al_InvOvld_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 462 | 0 / 1
855 | Al_InvOvld_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 463 | 0 / 1
856 | Al_InvOvld_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 464 | 0 / 1
857 | Al_InvOvld_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 465 | 0 / 1
858 | Al_InvOvld_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 466 | 0 / 1
859 | Al_InvOvld_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 467 | 0 / 1
860 | Al_LowSupplyTemp.Trigger | AL - Alarm - Probe - Low Supply Temperature [0 / 1] | BOOL | Read | Coil | 468 | 0 / 1
861 | Al_LowVolt_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Low Voltage [0 / 1] | BOOL | Read | Coil | 469 | 0 / 1
862 | Al_LowVolt_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Low Voltage [0 / 1] | BOOL | Read | Coil | 470 | 0 / 1
863 | Al_LowVolt_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Low Voltage [0 / 1] | BOOL | Read | Coil | 471 | 0 / 1
864 | Al_LowVolt_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Low Voltage [0 / 1] | BOOL | Read | Coil | 472 | 0 / 1
865 | Al_LowVolt_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Low Voltage [0 / 1] | BOOL | Read | Coil | 473 | 0 / 1
866 | Al_LowVolt_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Low Voltage [0 / 1] | BOOL | Read | Coil | 474 | 0 / 1
867 | Al_LowVolt_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Low Voltage [0 / 1] | BOOL | Read | Coil | 475 | 0 / 1
868 | Al_LowVolt_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Low Voltage [0 / 1] | BOOL | Read | Coil | 476 | 0 / 1
869 | Al_LowVolt_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Low Voltage [0 / 1] | BOOL | Read | Coil | 477 | 0 / 1
870 | Al_LowVolt_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Low Voltage [0 / 1] | BOOL | Read | Coil | 478 | 0 / 1
871 | Al_LowVolt_Rotary.Trigger | AL - Alarm - Rotary - Low Voltage [0 / 1] | BOOL | Read | Coil | 479 | 0 / 1
872 | Al_LowVolt_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Low Voltage [0 / 1] | BOOL | Read | Coil | 480 | 0 / 1
873 | Al_LowVolt_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Low Voltage [0 / 1] | BOOL | Read | Coil | 481 | 0 / 1
874 | Al_LowVolt_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Low Voltage [0 / 1] | BOOL | Read | Coil | 482 | 0 / 1
875 | Al_LowVolt_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Low Voltage [0 / 1] | BOOL | Read | Coil | 483 | 0 / 1
876 | Al_LowVolt_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Low Voltage [0 / 1] | BOOL | Read | Coil | 484 | 0 / 1
877 | Al_LowVolt_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Low Voltage [0 / 1] | BOOL | Read | Coil | 485 | 0 / 1
878 | Al_LowVolt_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Low Voltage [0 / 1] | BOOL | Read | Coil | 486 | 0 / 1
879 | Al_LowVolt_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Low Voltage [0 / 1] | BOOL | Read | Coil | 487 | 0 / 1
880 | Al_LowVolt_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Low Voltage [0 / 1] | BOOL | Read | Coil | 488 | 0 / 1
881 | Al_LowVolt_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Low Voltage [0 / 1] | BOOL | Read | Coil | 489 | 0 / 1
882 | Al_MB_AO1.Trigger | AL - Alarm - Control Circuit - AO1 [0 / 1] | BOOL | Read | Coil | 490 | 0 / 1
883 | Al_MB_AO1_AO4_PWM.Trigger | AL - Alarm - Control Circuit - AO1_AO4_PWM [0 / 1] | BOOL | Read | Coil | 491 | 0 / 1
884 | Al_MB_AO2.Trigger | AL - Alarm - Control Circuit - AO2 [0 / 1] | BOOL | Read | Coil | 492 | 0 / 1
885 | Al_MB_AO3.Trigger | AL - Alarm - Control Circuit - AO3 [0 / 1] | BOOL | Read | Coil | 493 | 0 / 1
886 | Al_MB_AO4.Trigger | AL - Alarm - Control Circuit - AO4 [0 / 1] | BOOL | Read | Coil | 494 | 0 / 1
887 | Al_MB_Control_Supply.Trigger | AL - Alarm - Control Circuit - Control_Supply [0 / 1] | BOOL | Read | Coil | 495 | 0 / 1
888 | Al_MB_Control_Temp.Trigger | AL - Alarm - Control Circuit - Control_Temp [0 / 1] | BOOL | Read | Coil | 496 | 0 / 1
889 | Al_MB_Humidity.Trigger | AL - Alarm - Control Circuit - Humidity [0 / 1] | BOOL | Read | Coil | 497 | 0 / 1
890 | Al_MB_Press_Fan_Return.Trigger | AL - Alarm - Control Circuit - Press_Fan_Return [0 / 1] | BOOL | Read | Coil | 498 | 0 / 1
891 | Al_MB_Press_Fan_Supply.Trigger | AL - Alarm - Control Circuit - Press_Fan_Supply [0 / 1] | BOOL | Read | Coil | 499 | 0 / 1
892 | Al_MB_Press_Filter_Return.Trigger | AL - Alarm - Control Circuit - Press_Filter_Return [0 / 1] | BOOL | Read | Coil | 500 | 0 / 1
893 | Al_MB_Press_Filter_Supply.Trigger | AL - Alarm - Control Circuit - Press_Filter_Supply [0 / 1] | BOOL | Read | Coil | 501 | 0 / 1
894 | Al_MB_Supply24.Trigger | AL - Alarm - Control Circuit - Supply24 [0 / 1] | BOOL | Read | Coil | 502 | 0 / 1
895 | Al_MB_Temp_Fan_Return.Trigger | AL - Alarm - Control Circuit - Temp_Fan_Return [0 / 1] | BOOL | Read | Coil | 503 | 0 / 1
896 | Al_MB_Temp_Fan_Supply.Trigger | AL - Alarm - Control Circuit - Temp_Fan_Supply [0 / 1] | BOOL | Read | Coil | 504 | 0 / 1
897 | Al_MB_Temp_Filter_Return.Trigger | AL - Alarm - Control Circuit - Temp_Filter_Return [0 / 1] | BOOL | Read | Coil | 505 | 0 / 1
898 | Al_MB_Temp_Filter_Supply.Trigger | AL - Alarm - Control Circuit - Temp_Filter_Supply [0 / 1] | BOOL | Read | Coil | 506 | 0 / 1
899 | Al_MB_Temperature.Trigger | AL - Alarm - Control Circuit - Temperature [0 / 1] | BOOL | Read | Coil | 507 | 0 / 1
900 | Al_MotorFault_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 508 | 0 / 1
901 | Al_MotorFault_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 509 | 0 / 1
902 | Al_MotorFault_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 510 | 0 / 1
903 | Al_MotorFault_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 511 | 0 / 1
904 | Al_MotorFault_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 512 | 0 / 1
905 | Al_MotorFault_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 513 | 0 / 1
906 | Al_MotorFault_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 514 | 0 / 1
907 | Al_MotorFault_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 515 | 0 / 1
908 | Al_MotorFault_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 516 | 0 / 1
909 | Al_MotorFault_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 517 | 0 / 1
910 | Al_MotorFault_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 518 | 0 / 1
911 | Al_MotorFault_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 519 | 0 / 1
912 | Al_MotorFault_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 520 | 0 / 1
913 | Al_MotorFault_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 521 | 0 / 1
914 | Al_MotorFault_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 522 | 0 / 1
915 | Al_MotorFault_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 523 | 0 / 1
916 | Al_MotorFault_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 524 | 0 / 1
917 | Al_MotorFault_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 525 | 0 / 1
918 | Al_MotorFault_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 526 | 0 / 1
919 | Al_MotorOverheat_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 527 | 0 / 1
920 | Al_MotorOverheat_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 528 | 0 / 1
921 | Al_MotorOverheat_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 529 | 0 / 1
922 | Al_MotorOverheat_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 530 | 0 / 1
923 | Al_MotorOverheat_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 531 | 0 / 1
924 | Al_MotorOverheat_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 532 | 0 / 1
925 | Al_MotorOverheat_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 533 | 0 / 1
926 | Al_MotorOverheat_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 534 | 0 / 1
927 | Al_MotorOverheat_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 535 | 0 / 1
928 | Al_MotorOverheat_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 536 | 0 / 1
929 | Al_MotorOverheat_Rotary.Trigger | AL - Alarm - Rotary - Motor Overheat [0 / 1] | BOOL | Read | Coil | 537 | 0 / 1
930 | Al_MotorOverheat_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 538 | 0 / 1
931 | Al_MotorOverheat_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 539 | 0 / 1
932 | Al_MotorOverheat_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 540 | 0 / 1
933 | Al_MotorOverheat_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 541 | 0 / 1
934 | Al_MotorOverheat_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 542 | 0 / 1
935 | Al_MotorOverheat_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 543 | 0 / 1
936 | Al_MotorOverheat_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 544 | 0 / 1
937 | Al_MotorOverheat_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 545 | 0 / 1
938 | Al_MotorOverheat_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 546 | 0 / 1
939 | Al_MotorOverheat_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 547 | 0 / 1
940 | Al_Offline_cpCOe.Trigger | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | BOOL | Read | Coil | 548 | 0 / 1
941 | Al_Offline_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Offline [0 / 1] | BOOL | Read | Coil | 549 | 0 / 1
942 | Al_Offline_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Offline [0 / 1] | BOOL | Read | Coil | 550 | 0 / 1
943 | Al_Offline_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Offline [0 / 1] | BOOL | Read | Coil | 551 | 0 / 1
944 | Al_Offline_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Offline [0 / 1] | BOOL | Read | Coil | 552 | 0 / 1
945 | Al_Offline_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Offline [0 / 1] | BOOL | Read | Coil | 553 | 0 / 1
946 | Al_Offline_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Offline [0 / 1] | BOOL | Read | Coil | 554 | 0 / 1
947 | Al_Offline_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Offline [0 / 1] | BOOL | Read | Coil | 555 | 0 / 1
948 | Al_Offline_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Offline [0 / 1] | BOOL | Read | Coil | 556 | 0 / 1
949 | Al_Offline_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Offline [0 / 1] | BOOL | Read | Coil | 557 | 0 / 1
950 | Al_Offline_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Offline [0 / 1] | BOOL | Read | Coil | 558 | 0 / 1
951 | Al_Offline_MainBoard.Trigger | AL - Alarm - Control Circuit - Offline [0 / 1] | BOOL | Read | Coil | 559 | 0 / 1
952 | Al_Offline_Rotary.Trigger | AL - Alarm - Rotary - Offline [0 / 1] | BOOL | Read | Coil | 560 | 0 / 1
953 | Al_Offline_SP_ExhHum.Trigger | AL - Alarm - Probe - Return Humidity - Offline [0 / 1] | BOOL | Read | Coil | 561 | 0 / 1
954 | Al_Offline_SP_ExhPress.Trigger | AL - Alarm - Probe - Return Air Pressure - Offline [0 / 1] | BOOL | Read | Coil | 562 | 0 / 1
955 | Al_Offline_SP_SupplyHum.Trigger | AL - Alarm - Probe - Supply humidity - Offline [0 / 1] | BOOL | Read | Coil | 563 | 0 / 1
956 | Al_Offline_SP_SupplyPress.Trigger | AL - Alarm - Probe - Supply Air Pressure - Offline [0 / 1] | BOOL | Read | Coil | 564 | 0 / 1
957 | Al_Offline_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Offline [0 / 1] | BOOL | Read | Coil | 565 | 0 / 1
958 | Al_Offline_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Offline [0 / 1] | BOOL | Read | Coil | 566 | 0 / 1
959 | Al_Offline_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Offline [0 / 1] | BOOL | Read | Coil | 567 | 0 / 1
960 | Al_Offline_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Offline [0 / 1] | BOOL | Read | Coil | 568 | 0 / 1
961 | Al_Offline_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Offline [0 / 1] | BOOL | Read | Coil | 569 | 0 / 1
962 | Al_Offline_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Offline [0 / 1] | BOOL | Read | Coil | 570 | 0 / 1
963 | Al_Offline_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Offline [0 / 1] | BOOL | Read | Coil | 571 | 0 / 1
964 | Al_Offline_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Offline [0 / 1] | BOOL | Read | Coil | 572 | 0 / 1
965 | Al_Offline_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Offline [0 / 1] | BOOL | Read | Coil | 573 | 0 / 1
966 | Al_Offline_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Offline [0 / 1] | BOOL | Read | Coil | 574 | 0 / 1
967 | Al_Offline_THTN_1.Trigger | AL - Alarm - HMI Basic - Offline [0 / 1] | BOOL | Read | Coil | 575 | 0 / 1
968 | Al_Option_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Option [0 / 1] | BOOL | Read | Coil | 576 | 0 / 1
969 | Al_Option_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Option [0 / 1] | BOOL | Read | Coil | 577 | 0 / 1
970 | Al_Option_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Option [0 / 1] | BOOL | Read | Coil | 578 | 0 / 1
971 | Al_Option_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Option [0 / 1] | BOOL | Read | Coil | 579 | 0 / 1
972 | Al_Option_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Option [0 / 1] | BOOL | Read | Coil | 580 | 0 / 1
973 | Al_Option_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Option [0 / 1] | BOOL | Read | Coil | 581 | 0 / 1
974 | Al_Option_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Option [0 / 1] | BOOL | Read | Coil | 582 | 0 / 1
975 | Al_Option_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Option [0 / 1] | BOOL | Read | Coil | 583 | 0 / 1
976 | Al_Option_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Option [0 / 1] | BOOL | Read | Coil | 584 | 0 / 1
977 | Al_Option_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Option [0 / 1] | BOOL | Read | Coil | 585 | 0 / 1
978 | Al_Option_Rotary.Trigger | AL - Alarm - Rotary - Option [0 / 1] | BOOL | Read | Coil | 586 | 0 / 1
979 | Al_Option_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Option [0 / 1] | BOOL | Read | Coil | 587 | 0 / 1
980 | Al_Option_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Option [0 / 1] | BOOL | Read | Coil | 588 | 0 / 1
981 | Al_Option_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Option [0 / 1] | BOOL | Read | Coil | 589 | 0 / 1
982 | Al_Option_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Option [0 / 1] | BOOL | Read | Coil | 590 | 0 / 1
983 | Al_Option_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Option [0 / 1] | BOOL | Read | Coil | 591 | 0 / 1
984 | Al_Option_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Option [0 / 1] | BOOL | Read | Coil | 592 | 0 / 1
985 | Al_Option_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Option [0 / 1] | BOOL | Read | Coil | 593 | 0 / 1
986 | Al_Option_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Option [0 / 1] | BOOL | Read | Coil | 594 | 0 / 1
987 | Al_Option_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Option [0 / 1] | BOOL | Read | Coil | 595 | 0 / 1
988 | Al_Option_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Option [0 / 1] | BOOL | Read | Coil | 596 | 0 / 1
989 | Al_Overcurrent_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Over Current [0 / 1] | BOOL | Read | Coil | 597 | 0 / 1
990 | Al_Overcurrent_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Over Current [0 / 1] | BOOL | Read | Coil | 598 | 0 / 1
991 | Al_Overcurrent_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Over Current [0 / 1] | BOOL | Read | Coil | 599 | 0 / 1
992 | Al_Overcurrent_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Over Current [0 / 1] | BOOL | Read | Coil | 600 | 0 / 1
993 | Al_Overcurrent_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Over Current [0 / 1] | BOOL | Read | Coil | 601 | 0 / 1
994 | Al_Overcurrent_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Over current [0 / 1] | BOOL | Read | Coil | 602 | 0 / 1
995 | Al_Overcurrent_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Over Current [0 / 1] | BOOL | Read | Coil | 603 | 0 / 1
996 | Al_Overcurrent_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Over Current [0 / 1] | BOOL | Read | Coil | 604 | 0 / 1
997 | Al_Overcurrent_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Over Current [0 / 1] | BOOL | Read | Coil | 605 | 0 / 1
998 | Al_Overcurrent_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Over Current [0 / 1] | BOOL | Read | Coil | 606 | 0 / 1
999 | Al_Overcurrent_Rotary.Trigger | AL - Alarm - Rotary - OverCurrent [0 / 1] | BOOL | Read | Coil | 607 | 0 / 1
1000 | Al_Overcurrent_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Over current [0 / 1] | BOOL | Read | Coil | 608 | 0 / 1
1001 | Al_Overcurrent_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Over Current [0 / 1] | BOOL | Read | Coil | 609 | 0 / 1
1002 | Al_Overcurrent_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Over Current [0 / 1] | BOOL | Read | Coil | 610 | 0 / 1
1003 | Al_Overcurrent_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Over Current [0 / 1] | BOOL | Read | Coil | 611 | 0 / 1
1004 | Al_Overcurrent_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Over Current [0 / 1] | BOOL | Read | Coil | 612 | 0 / 1
1005 | Al_Overcurrent_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Over current [0 / 1] | BOOL | Read | Coil | 613 | 0 / 1
1006 | Al_Overcurrent_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Over Current [0 / 1] | BOOL | Read | Coil | 614 | 0 / 1
1007 | Al_Overcurrent_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Over Current [0 / 1] | BOOL | Read | Coil | 615 | 0 / 1
1008 | Al_Overcurrent_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Over Current [0 / 1] | BOOL | Read | Coil | 616 | 0 / 1
1009 | Al_Overcurrent_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Over Current [0 / 1] | BOOL | Read | Coil | 617 | 0 / 1
1010 | Al_OverVolt_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Over Voltage [0 / 1] | BOOL | Read | Coil | 618 | 0 / 1
1011 | Al_OverVolt_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Over Voltage [0 / 1] | BOOL | Read | Coil | 619 | 0 / 1
1012 | Al_OverVolt_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Over Voltage [0 / 1] | BOOL | Read | Coil | 620 | 0 / 1
1013 | Al_OverVolt_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Over Voltage [0 / 1] | BOOL | Read | Coil | 621 | 0 / 1
1014 | Al_OverVolt_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Over Voltage [0 / 1] | BOOL | Read | Coil | 622 | 0 / 1
1015 | Al_OverVolt_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Over voltage [0 / 1] | BOOL | Read | Coil | 623 | 0 / 1
1016 | Al_OverVolt_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Over Voltage [0 / 1] | BOOL | Read | Coil | 624 | 0 / 1
1017 | Al_OverVolt_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Over Voltage [0 / 1] | BOOL | Read | Coil | 625 | 0 / 1
1018 | Al_OverVolt_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Over Voltage [0 / 1] | BOOL | Read | Coil | 626 | 0 / 1
1019 | Al_OverVolt_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Over Voltage [0 / 1] | BOOL | Read | Coil | 627 | 0 / 1
1020 | Al_OverVolt_Rotary.Trigger | AL - Alarm - Rotary - OverVoltage [0 / 1] | BOOL | Read | Coil | 628 | 0 / 1
1021 | Al_OverVolt_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Over voltage [0 / 1] | BOOL | Read | Coil | 629 | 0 / 1
1022 | Al_OverVolt_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Over Voltage [0 / 1] | BOOL | Read | Coil | 630 | 0 / 1
1023 | Al_OverVolt_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Over Voltage [0 / 1] | BOOL | Read | Coil | 631 | 0 / 1
1024 | Al_OverVolt_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Over Voltage [0 / 1] | BOOL | Read | Coil | 632 | 0 / 1
1025 | Al_OverVolt_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Over Voltage [0 / 1] | BOOL | Read | Coil | 633 | 0 / 1
1026 | Al_OverVolt_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Over voltage [0 / 1] | BOOL | Read | Coil | 634 | 0 / 1
1027 | Al_OverVolt_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Over Voltage [0 / 1] | BOOL | Read | Coil | 635 | 0 / 1
1028 | Al_OverVolt_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Over Voltage [0 / 1] | BOOL | Read | Coil | 636 | 0 / 1
1029 | Al_OverVolt_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Over Voltage [0 / 1] | BOOL | Read | Coil | 637 | 0 / 1
1030 | Al_OverVolt_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Over Voltage [0 / 1] | BOOL | Read | Coil | 638 | 0 / 1
1031 | AL_Overvoltage_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 639 | 0 / 1
1032 | AL_Overvoltage_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 640 | 0 / 1
1033 | AL_Overvoltage_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 641 | 0 / 1
1034 | AL_Overvoltage_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 642 | 0 / 1
1035 | AL_Overvoltage_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 643 | 0 / 1
1036 | AL_Overvoltage_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 644 | 0 / 1
1037 | AL_Overvoltage_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 645 | 0 / 1
1038 | AL_Overvoltage_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 646 | 0 / 1
1039 | AL_Overvoltage_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 647 | 0 / 1
1040 | AL_Overvoltage_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 648 | 0 / 1
1041 | AL_Overvoltage_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 649 | 0 / 1
1042 | AL_Overvoltage_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 650 | 0 / 1
1043 | AL_Overvoltage_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 651 | 0 / 1
1044 | AL_Overvoltage_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 652 | 0 / 1
1045 | AL_Overvoltage_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 653 | 0 / 1
1046 | AL_Overvoltage_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 654 | 0 / 1
1047 | AL_Overvoltage_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 655 | 0 / 1
1048 | AL_Overvoltage_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 656 | 0 / 1
1049 | AL_Overvoltage_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 657 | 0 / 1
1050 | AL_Overvoltage_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 658 | 0 / 1
1051 | Al_Ovld_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Over Load [0 / 1] | BOOL | Read | Coil | 659 | 0 / 1
1052 | Al_Ovld_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Over Load [0 / 1] | BOOL | Read | Coil | 660 | 0 / 1
1053 | Al_Ovld_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Over Load [0 / 1] | BOOL | Read | Coil | 661 | 0 / 1
1054 | Al_Ovld_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Over Load [0 / 1] | BOOL | Read | Coil | 662 | 0 / 1
1055 | Al_Ovld_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Over Load [0 / 1] | BOOL | Read | Coil | 663 | 0 / 1
1056 | Al_Ovld_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Over load [0 / 1] | BOOL | Read | Coil | 664 | 0 / 1
1057 | Al_Ovld_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Over Load [0 / 1] | BOOL | Read | Coil | 665 | 0 / 1
1058 | Al_Ovld_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Over Load [0 / 1] | BOOL | Read | Coil | 666 | 0 / 1
1059 | Al_Ovld_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Over Load [0 / 1] | BOOL | Read | Coil | 667 | 0 / 1
1060 | Al_Ovld_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Over Load [0 / 1] | BOOL | Read | Coil | 668 | 0 / 1
1061 | Al_Ovld_Rotary.Trigger | AL - Alarm - Rotary - OverLoad [0 / 1] | BOOL | Read | Coil | 669 | 0 / 1
1062 | Al_Ovld_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Over load [0 / 1] | BOOL | Read | Coil | 670 | 0 / 1
1063 | Al_Ovld_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Over Load [0 / 1] | BOOL | Read | Coil | 671 | 0 / 1
1064 | Al_Ovld_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Over Load [0 / 1] | BOOL | Read | Coil | 672 | 0 / 1
1065 | Al_Ovld_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Over Load [0 / 1] | BOOL | Read | Coil | 673 | 0 / 1
1066 | Al_Ovld_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Over Load [0 / 1] | BOOL | Read | Coil | 674 | 0 / 1
1067 | Al_Ovld_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Over load [0 / 1] | BOOL | Read | Coil | 675 | 0 / 1
1068 | Al_Ovld_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Over Load [0 / 1] | BOOL | Read | Coil | 676 | 0 / 1
1069 | Al_Ovld_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Over Load [0 / 1] | BOOL | Read | Coil | 677 | 0 / 1
1070 | Al_Ovld_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Over Load [0 / 1] | BOOL | Read | Coil | 678 | 0 / 1
1071 | Al_Ovld_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Over Load [0 / 1] | BOOL | Read | Coil | 679 | 0 / 1
1072 | Al_ParamErr_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Parameters Error [0 / 1] | BOOL | Read | Coil | 680 | 0 / 1
1073 | Al_ParamErr_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Parameters Error [0 / 1] | BOOL | Read | Coil | 681 | 0 / 1
1074 | Al_ParamErr_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Parameters Error [0 / 1] | BOOL | Read | Coil | 682 | 0 / 1
1075 | Al_ParamErr_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Parameters Error [0 / 1] | BOOL | Read | Coil | 683 | 0 / 1
1076 | Al_ParamErr_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Parameters Error [0 / 1] | BOOL | Read | Coil | 684 | 0 / 1
1077 | Al_ParamErr_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 685 | 0 / 1
1078 | Al_ParamErr_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Parameters Error [0 / 1] | BOOL | Read | Coil | 686 | 0 / 1
1079 | Al_ParamErr_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Parameters Error [0 / 1] | BOOL | Read | Coil | 687 | 0 / 1
1080 | Al_ParamErr_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Parameters Error [0 / 1] | BOOL | Read | Coil | 688 | 0 / 1
1081 | Al_ParamErr_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Parameters Error [0 / 1] | BOOL | Read | Coil | 689 | 0 / 1
1082 | Al_ParamErr_Rotary.Trigger | AL - Alarm - Rotary - Parameters Error [0 / 1] | BOOL | Read | Coil | 690 | 0 / 1
1083 | Al_ParamErr_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 691 | 0 / 1
1084 | Al_ParamErr_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Parameters Error [0 / 1] | BOOL | Read | Coil | 692 | 0 / 1
1085 | Al_ParamErr_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Parameters Error [0 / 1] | BOOL | Read | Coil | 693 | 0 / 1
1086 | Al_ParamErr_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Parameters Error [0 / 1] | BOOL | Read | Coil | 694 | 0 / 1
1087 | Al_ParamErr_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Parameters Error [0 / 1] | BOOL | Read | Coil | 695 | 0 / 1
1088 | Al_ParamErr_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 696 | 0 / 1
1089 | Al_ParamErr_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Parameters Error [0 / 1] | BOOL | Read | Coil | 697 | 0 / 1
1090 | Al_ParamErr_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Parameters Error [0 / 1] | BOOL | Read | Coil | 698 | 0 / 1
1091 | Al_ParamErr_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Parameters Error [0 / 1] | BOOL | Read | Coil | 699 | 0 / 1
1092 | Al_ParamErr_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Parameters Error [0 / 1] | BOOL | Read | Coil | 700 | 0 / 1
1093 | AL_ParametersCRC_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 701 | 0 / 1
1094 | AL_ParametersCRC_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 702 | 0 / 1
1095 | AL_ParametersCRC_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 703 | 0 / 1
1096 | AL_ParametersCRC_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 704 | 0 / 1
1097 | AL_ParametersCRC_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 705 | 0 / 1
1098 | AL_ParametersCRC_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 706 | 0 / 1
1099 | AL_ParametersCRC_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 707 | 0 / 1
1100 | AL_ParametersCRC_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 708 | 0 / 1
1101 | AL_ParametersCRC_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 709 | 0 / 1
1102 | AL_ParametersCRC_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 710 | 0 / 1
1103 | AL_ParametersCRC_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 711 | 0 / 1
1104 | AL_ParametersCRC_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 712 | 0 / 1
1105 | AL_ParametersCRC_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 713 | 0 / 1
1106 | AL_ParametersCRC_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 714 | 0 / 1
1107 | AL_ParametersCRC_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 715 | 0 / 1
1108 | AL_ParametersCRC_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 716 | 0 / 1
1109 | AL_ParametersCRC_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 717 | 0 / 1
1110 | AL_ParametersCRC_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 718 | 0 / 1
1111 | AL_ParametersCRC_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 719 | 0 / 1
1112 | AL_ParametersCRC_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 720 | 0 / 1
1113 | AL_PhaseLoss_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 721 | 0 / 1
1114 | AL_PhaseLoss_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 722 | 0 / 1
1115 | AL_PhaseLoss_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 723 | 0 / 1
1116 | AL_PhaseLoss_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 724 | 0 / 1
1117 | AL_PhaseLoss_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 725 | 0 / 1
1118 | AL_PhaseLoss_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 726 | 0 / 1
1119 | AL_PhaseLoss_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 727 | 0 / 1
1120 | AL_PhaseLoss_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 728 | 0 / 1
1121 | AL_PhaseLoss_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 729 | 0 / 1
1122 | AL_PhaseLoss_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 730 | 0 / 1
1123 | AL_PhaseLoss_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 731 | 0 / 1
1124 | AL_PhaseLoss_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 732 | 0 / 1
1125 | AL_PhaseLoss_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 733 | 0 / 1
1126 | AL_PhaseLoss_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 734 | 0 / 1
1127 | AL_PhaseLoss_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 735 | 0 / 1
1128 | AL_PhaseLoss_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 736 | 0 / 1
1129 | AL_PhaseLoss_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 737 | 0 / 1
1130 | AL_PhaseLoss_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 738 | 0 / 1
1131 | AL_PhaseLoss_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 739 | 0 / 1
1132 | AL_PhaseLoss_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 740 | 0 / 1
1133 | Al_PhLost_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Phase Lost [0 / 1] | BOOL | Read | Coil | 741 | 0 / 1
1134 | Al_PhLost_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Phase Lost [0 / 1] | BOOL | Read | Coil | 742 | 0 / 1
1135 | Al_PhLost_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Phase Lost [0 / 1] | BOOL | Read | Coil | 743 | 0 / 1
1136 | Al_PhLost_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Phase Lost [0 / 1] | BOOL | Read | Coil | 744 | 0 / 1
1137 | Al_PhLost_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Phase Lost [0 / 1] | BOOL | Read | Coil | 745 | 0 / 1
1138 | Al_PhLost_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Phase Lost [0 / 1] | BOOL | Read | Coil | 746 | 0 / 1
1139 | Al_PhLost_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Phase Lost [0 / 1] | BOOL | Read | Coil | 747 | 0 / 1
1140 | Al_PhLost_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Phase Lost [0 / 1] | BOOL | Read | Coil | 748 | 0 / 1
1141 | Al_PhLost_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Phase Lost [0 / 1] | BOOL | Read | Coil | 749 | 0 / 1
1142 | Al_PhLost_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Phase Lost [0 / 1] | BOOL | Read | Coil | 750 | 0 / 1
1143 | Al_PhLost_Rotary.Trigger | AL - Alarm - Rotary - Phase Lost [0 / 1] | BOOL | Read | Coil | 751 | 0 / 1
1144 | Al_PhLost_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Phase Lost [0 / 1] | BOOL | Read | Coil | 752 | 0 / 1
1145 | Al_PhLost_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Phase Lost [0 / 1] | BOOL | Read | Coil | 753 | 0 / 1
1146 | Al_PhLost_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Phase Lost [0 / 1] | BOOL | Read | Coil | 754 | 0 / 1
1147 | Al_PhLost_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Phase Lost [0 / 1] | BOOL | Read | Coil | 755 | 0 / 1
1148 | Al_PhLost_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Phase Lost [0 / 1] | BOOL | Read | Coil | 756 | 0 / 1
1149 | Al_PhLost_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Phase Lost [0 / 1] | BOOL | Read | Coil | 757 | 0 / 1
1150 | Al_PhLost_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Phase Lost [0 / 1] | BOOL | Read | Coil | 758 | 0 / 1
1151 | Al_PhLost_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Phase Lost [0 / 1] | BOOL | Read | Coil | 759 | 0 / 1
1152 | Al_PhLost_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Phase Lost [0 / 1] | BOOL | Read | Coil | 760 | 0 / 1
1153 | Al_PhLost_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Phase Lost [0 / 1] | BOOL | Read | Coil | 761 | 0 / 1
1154 | Al_PhOpen_ExhFan_1.Trigger | AL - Alarm - Fan Return 1 - Phase Open [0 / 1] | BOOL | Read | Coil | 762 | 0 / 1
1155 | Al_PhOpen_ExhFan_10.Trigger | AL - Alarm - Fan Return 10 - Phase Open [0 / 1] | BOOL | Read | Coil | 763 | 0 / 1
1156 | Al_PhOpen_ExhFan_2.Trigger | AL - Alarm - Fan Return 2 - Phase Open [0 / 1] | BOOL | Read | Coil | 764 | 0 / 1
1157 | Al_PhOpen_ExhFan_3.Trigger | AL - Alarm - Fan Return 3 - Phase Open [0 / 1] | BOOL | Read | Coil | 765 | 0 / 1
1158 | Al_PhOpen_ExhFan_4.Trigger | AL - Alarm - Fan Return 4 - Phase Open [0 / 1] | BOOL | Read | Coil | 766 | 0 / 1
1159 | Al_PhOpen_ExhFan_5.Trigger | AL - Alarm - Fan Return 5 - Phase Open [0 / 1] | BOOL | Read | Coil | 767 | 0 / 1
1160 | Al_PhOpen_ExhFan_6.Trigger | AL - Alarm - Fan Return 6 - Phase Open [0 / 1] | BOOL | Read | Coil | 768 | 0 / 1
1161 | Al_PhOpen_ExhFan_7.Trigger | AL - Alarm - Fan Return 7 - Phase Open [0 / 1] | BOOL | Read | Coil | 769 | 0 / 1
1162 | Al_PhOpen_ExhFan_8.Trigger | AL - Alarm - Fan Return 8 - Phase Open [0 / 1] | BOOL | Read | Coil | 770 | 0 / 1
1163 | Al_PhOpen_ExhFan_9.Trigger | AL - Alarm - Fan Return 9 - Phase Open [0 / 1] | BOOL | Read | Coil | 771 | 0 / 1
1164 | Al_PhOpen_Rotary.Trigger | AL - Alarm - Rotary - Phase Open [0 / 1] | BOOL | Read | Coil | 772 | 0 / 1
1165 | Al_PhOpen_SupFan_1.Trigger | AL - Alarm - Fan Supply 1 - Phase Open [0 / 1] | BOOL | Read | Coil | 773 | 0 / 1
1166 | Al_PhOpen_SupFan_10.Trigger | AL - Alarm - Fan Supply 10 - Phase Open [0 / 1] | BOOL | Read | Coil | 774 | 0 / 1
1167 | Al_PhOpen_SupFan_2.Trigger | AL - Alarm - Fan Supply 2 - Phase Open [0 / 1] | BOOL | Read | Coil | 775 | 0 / 1
1168 | Al_PhOpen_SupFan_3.Trigger | AL - Alarm - Fan Supply 3 - Phase Open [0 / 1] | BOOL | Read | Coil | 776 | 0 / 1
1169 | Al_PhOpen_SupFan_4.Trigger | AL - Alarm - Fan Supply 4 - Phase Open [0 / 1] | BOOL | Read | Coil | 777 | 0 / 1
1170 | Al_PhOpen_SupFan_5.Trigger | AL - Alarm - Fan Supply 5 - Phase Open [0 / 1] | BOOL | Read | Coil | 778 | 0 / 1
1171 | Al_PhOpen_SupFan_6.Trigger | AL - Alarm - Fan Supply 6 - Phase Open [0 / 1] | BOOL | Read | Coil | 779 | 0 / 1
1172 | Al_PhOpen_SupFan_7.Trigger | AL - Alarm - Fan Supply 7 - Phase Open [0 / 1] | BOOL | Read | Coil | 780 | 0 / 1
1173 | Al_PhOpen_SupFan_8.Trigger | AL - Alarm - Fan Supply 8 - Phase Open [0 / 1] | BOOL | Read | Coil | 781 | 0 / 1
1174 | Al_PhOpen_SupFan_9.Trigger | AL - Alarm - Fan Supply 9 - Phase Open [0 / 1] | BOOL | Read | Coil | 782 | 0 / 1
1175 | Al_PreHeatCoilTempPrb.Trigger | AL - Alarm - Probe - Temperature Water PreHeating Coil [0 / 1] | BOOL | Read | Coil | 783 | 0 / 1
1176 | Al_RDT_Fan.Trigger | AL - Alarm - Fan Group [0 / 1] | BOOL | Read | Coil | 784 | 0 / 1
1177 | Al_RecSupplyTemp.Trigger | AL - Alarm - Probe - Supply Recovery Temperature [0 / 1] | BOOL | Read | Coil | 785 | 0 / 1
1178 | Al_ReheatCoilWorkHrsWarn.Trigger | AL - Alarm - ReHeatCoil - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 786 | 0 / 1
1179 | Al_retain.Trigger | AL - Alarm - Retain [0 / 1] | BOOL | Read | Coil | 787 | 0 / 1
1180 | Al_RetAir_CO2_Lev_Prb.Trigger | AL - Alarm - Probe - CO2 Return Level Probe [0 / 1] | BOOL | Read | Coil | 788 | 0 / 1
1181 | Al_RetAirFlwSwWarn.Trigger | AL - Alarm - Probe - Air Flow Return SW Warning [0 / 1] | BOOL | Read | Coil | 789 | 0 / 1
1182 | Al_RetAirP_Prb.Trigger | AL - Alarm - Probe - Pressure Return Air [0 / 1] | BOOL | Read | Coil | 790 | 0 / 1
1183 | Al_RetFanWorkHrsWarn.Trigger | AL - Alarm - Fan Return - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 791 | 0 / 1
1184 | Al_RetFilt.Trigger | AL - Alarm - Filter - Return [0 / 1] | BOOL | Read | Coil | 792 | 0 / 1
1185 | Al_RetTempPrb.Trigger | AL - Alarm - Probe - Return Temperature [0 / 1] | BOOL | Read | Coil | 793 | 0 / 1
1186 | Al_SupplyAirFlwSwWarn.Trigger | AL - Alarm - Probe - Supply Air Flow SW Warning [0 / 1] | BOOL | Read | Coil | 794 | 0 / 1
1187 | Al_SupplyAirP_Prb.Trigger | AL - Alarm - Probe - Supply Air Pressure [0 / 1] | BOOL | Read | Coil | 795 | 0 / 1
1188 | Al_SupplyFanWorkHrsWarn.Trigger | AL - Alarm - Fan Supply - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 796 | 0 / 1
1189 | Al_SupplyFilt.Trigger | AL - Alarm - Filter - Supply [0 / 1] | BOOL | Read | Coil | 797 | 0 / 1
1190 | Al_SupplyTempPrb.Trigger | AL - Alarm - Probe - Supply Temperature [0 / 1] | BOOL | Read | Coil | 798 | 0 / 1
1191 | Al_SwPrototype.Trigger | AL - Alarm - Software Version - Prototype [0 / 1] | BOOL | Read | Coil | 799 | 0 / 1
1192 | Al_ThTune_ClkBrd.Trigger | AL - Alarm - HMI Basic - Clock Board [0 / 1] | BOOL | Read | Coil | 800 | 0 / 1
1193 | Al_ThTune_HumPrb.Trigger | AL - Alarm - HMI Basic - Humidity Probe [0 / 1] | BOOL | Read | Coil | 801 | 0 / 1
1194 | Al_ThTune_TempPrb.Trigger | AL - Alarm - HMI Basic - Temperature Probe [0 / 1] | BOOL | Read | Coil | 802 | 0 / 1
1195 | Al_TooHot_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - TooHot [0 / 1] | BOOL | Read | Coil | 803 | 0 / 1
1196 | Al_TooHot_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - TooHot [0 / 1] | BOOL | Read | Coil | 804 | 0 / 1
1197 | Al_TooHot_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - TooHot [0 / 1] | BOOL | Read | Coil | 805 | 0 / 1
1198 | Al_TooHot_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - TooHot [0 / 1] | BOOL | Read | Coil | 806 | 0 / 1
1199 | Al_TooHot_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - TooHot [0 / 1] | BOOL | Read | Coil | 807 | 0 / 1
1200 | Al_TooHot_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - TooHot [0 / 1] | BOOL | Read | Coil | 808 | 0 / 1
1201 | Al_TooHot_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - TooHot [0 / 1] | BOOL | Read | Coil | 809 | 0 / 1
1202 | Al_TooHot_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - TooHot [0 / 1] | BOOL | Read | Coil | 810 | 0 / 1
1203 | Al_TooHot_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - TooHot [0 / 1] | BOOL | Read | Coil | 811 | 0 / 1
1204 | Al_TooHot_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - TooHot [0 / 1] | BOOL | Read | Coil | 812 | 0 / 1
1205 | Al_TooHot_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - TooHot [0 / 1] | BOOL | Read | Coil | 813 | 0 / 1
1206 | Al_TooHot_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - TooHot [0 / 1] | BOOL | Read | Coil | 814 | 0 / 1
1207 | Al_TooHot_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - TooHot [0 / 1] | BOOL | Read | Coil | 815 | 0 / 1
1208 | Al_TooHot_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - TooHot [0 / 1] | BOOL | Read | Coil | 816 | 0 / 1
1209 | Al_TooHot_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - TooHot [0 / 1] | BOOL | Read | Coil | 817 | 0 / 1
1210 | Al_TooHot_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - TooHot [0 / 1] | BOOL | Read | Coil | 818 | 0 / 1
1211 | Al_TooHot_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - TooHot [0 / 1] | BOOL | Read | Coil | 819 | 0 / 1
1212 | Al_TooHot_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - TooHot [0 / 1] | BOOL | Read | Coil | 820 | 0 / 1
1213 | Al_TooHot_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - TooHot [0 / 1] | BOOL | Read | Coil | 821 | 0 / 1
1214 | Al_TooHot_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - TooHot [0 / 1] | BOOL | Read | Coil | 822 | 0 / 1
1215 | Al_Undervoltage_EC_ExhFan1.Trigger | AL - Alarm - Fan Return 1 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 823 | 0 / 1
1216 | Al_Undervoltage_EC_ExhFan10.Trigger | AL - Alarm - Fan Return 10 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 824 | 0 / 1
1217 | Al_Undervoltage_EC_ExhFan2.Trigger | AL - Alarm - Fan Return 2 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 825 | 0 / 1
1218 | Al_Undervoltage_EC_ExhFan3.Trigger | AL - Alarm - Fan Return 3 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 826 | 0 / 1
1219 | Al_Undervoltage_EC_ExhFan4.Trigger | AL - Alarm - Fan Return 4 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 827 | 0 / 1
1220 | Al_Undervoltage_EC_ExhFan5.Trigger | AL - Alarm - Fan Return 5 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 828 | 0 / 1
1221 | Al_Undervoltage_EC_ExhFan6.Trigger | AL - Alarm - Fan Return 6 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 829 | 0 / 1
1222 | Al_Undervoltage_EC_ExhFan7.Trigger | AL - Alarm - Fan Return 7 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 830 | 0 / 1
1223 | Al_Undervoltage_EC_ExhFan8.Trigger | AL - Alarm - Fan Return 8 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 831 | 0 / 1
1224 | Al_Undervoltage_EC_ExhFan9.Trigger | AL - Alarm - Fan Return 9 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 832 | 0 / 1
1225 | Al_Undervoltage_EC_SupFan1.Trigger | AL - Alarm - Fan Supply 1 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 833 | 0 / 1
1226 | Al_Undervoltage_EC_SupFan10.Trigger | AL - Alarm - Fan Supply 10 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 834 | 0 / 1
1227 | Al_Undervoltage_EC_SupFan2.Trigger | AL - Alarm - Fan Supply 2 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 835 | 0 / 1
1228 | Al_Undervoltage_EC_SupFan3.Trigger | AL - Alarm - Fan Supply 3 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 836 | 0 / 1
1229 | Al_Undervoltage_EC_SupFan4.Trigger | AL - Alarm - Fan Supply 4 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 837 | 0 / 1
1230 | Al_Undervoltage_EC_SupFan5.Trigger | AL - Alarm - Fan Supply 5 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 838 | 0 / 1
1231 | Al_Undervoltage_EC_SupFan6.Trigger | AL - Alarm - Fan Supply 6 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 839 | 0 / 1
1232 | Al_Undervoltage_EC_SupFan7.Trigger | AL - Alarm - Fan Supply 7 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 840 | 0 / 1
1233 | Al_Undervoltage_EC_SupFan8.Trigger | AL - Alarm - Fan Supply 8 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 841 | 0 / 1
1234 | Al_Undervoltage_EC_SupFan9.Trigger | AL - Alarm - Fan Supply 9 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 842 | 0 / 1
1235 | CfgErrAlrm.Trigger | AL - Alarm - Device - Wrong configuration [0 / 1] | BOOL | Read | Coil | 843 | 0 / 1
1236 | OfflineAlrm.Trigger | AL - Alarm - Device - Offline [0 / 1] | BOOL | Read | Coil | 844 | 0 / 1
1237 | AlarmMng.AlrmResByBms | AL - Alarm - BMS - Reset [0 / 1] | BOOL | ReadWrite | Coil | 845 | 0 / 1 | 0 - 1 - RESET
1238 | Al_ABB_ExhFan_1.Active | AL - Alarm - Fan Return 1 [0 / 1] | BOOL | Read | Coil | 846 | 0 / 1
1239 | Al_ABB_ExhFan_10.Active | AL - Alarm - Fan Return 10 [0 / 1] | BOOL | Read | Coil | 847 | 0 / 1
1240 | Al_ABB_ExhFan_2.Active | AL - Alarm - Fan Return 2 [0 / 1] | BOOL | Read | Coil | 848 | 0 / 1
1241 | Al_ABB_ExhFan_3.Active | AL - Alarm - Fan Return 3 [0 / 1] | BOOL | Read | Coil | 849 | 0 / 1
1242 | Al_ABB_ExhFan_4.Active | AL - Alarm - Fan Return 4 [0 / 1] | BOOL | Read | Coil | 850 | 0 / 1
1243 | Al_ABB_ExhFan_5.Active | AL - Alarm - Fan Return 5 [0 / 1] | BOOL | Read | Coil | 851 | 0 / 1
1244 | Al_ABB_ExhFan_6.Active | AL - Alarm - Fan Return 6 [0 / 1] | BOOL | Read | Coil | 852 | 0 / 1
1245 | Al_ABB_ExhFan_7.Active | AL - Alarm - Fan Return 7 [0 / 1] | BOOL | Read | Coil | 853 | 0 / 1
1246 | Al_ABB_ExhFan_8.Active | AL - Alarm - Fan Return 8 [0 / 1] | BOOL | Read | Coil | 854 | 0 / 1
1247 | Al_ABB_ExhFan_9.Active | AL - Alarm - Fan Return 9 [0 / 1] | BOOL | Read | Coil | 855 | 0 / 1
1248 | Al_ABB_Rotary.Active | AL - Alarm - Rotary [0 / 1] | BOOL | Read | Coil | 856 | 0 / 1
1249 | Al_ABB_SupFan_1.Active | AL - Alarm - Fan Supply 1 [0 / 1] | BOOL | Read | Coil | 857 | 0 / 1
1250 | Al_ABB_SupFan_10.Active | AL - Alarm - Fan Supply 10 [0 / 1] | BOOL | Read | Coil | 858 | 0 / 1
1251 | Al_ABB_SupFan_2.Active | AL - Alarm - Fan Supply 2 [0 / 1] | BOOL | Read | Coil | 859 | 0 / 1
1252 | Al_ABB_SupFan_3.Active | AL - Alarm - Fan Supply 3 [0 / 1] | BOOL | Read | Coil | 860 | 0 / 1
1253 | Al_ABB_SupFan_4.Active | AL - Alarm - Fan Supply 4 [0 / 1] | BOOL | Read | Coil | 861 | 0 / 1
1254 | Al_ABB_SupFan_5.Active | AL - Alarm - Fan Supply 5 [0 / 1] | BOOL | Read | Coil | 862 | 0 / 1
1255 | Al_ABB_SupFan_6.Active | AL - Alarm - Fan Supply 6 [0 / 1] | BOOL | Read | Coil | 863 | 0 / 1
1256 | Al_ABB_SupFan_7.Active | AL - Alarm - Fan Supply 7 [0 / 1] | BOOL | Read | Coil | 864 | 0 / 1
1257 | Al_ABB_SupFan_8.Active | AL - Alarm - Fan Supply 8 [0 / 1] | BOOL | Read | Coil | 865 | 0 / 1
1258 | Al_ABB_SupFan_9.Active | AL - Alarm - Fan Supply 9 [0 / 1] | BOOL | Read | Coil | 866 | 0 / 1
1259 | Al_AFreezeDIN.Active | AL - Alarm - Antifreeze - Digital Input [0 / 1] | BOOL | Read | Coil | 867 | 0 / 1
1260 | Al_AFreezePRB.Active | AL - Alarm - Antifreeze - Back Water Temperature [0 / 1] | BOOL | Read | Coil | 868 | 0 / 1
1261 | Al_AFreezePreHeatPRB.Active | AL - Alarm - Antifreeze - PreHeat Back Water Temperature [0 / 1] | BOOL | Read | Coil | 869 | 0 / 1
1262 | Al_AfterPreHeatCoilTempPrb.Active | AL - Alarm - Probe - After preheating coil temperature [0 / 1] | BOOL | Read | Coil | 870 | 0 / 1
1263 | Al_BMS_Offline.Active | AL - Alarm - BMS - Offline [0 / 1] | BOOL | Read | Coil | 871 | 0 / 1
1264 | Al_CfgError_cpCOe.Active | AL - Alarm - Module IO - cPCOE - Configuration error [0 / 1] | BOOL | Read | Coil | 872 | 0 / 1
1265 | Al_CircuitFault_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 873 | 0 / 1
1266 | Al_CircuitFault_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 874 | 0 / 1
1267 | Al_CircuitFault_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 875 | 0 / 1
1268 | Al_CircuitFault_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 876 | 0 / 1
1269 | Al_CircuitFault_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 877 | 0 / 1
1270 | Al_CircuitFault_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 878 | 0 / 1
1271 | Al_CircuitFault_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 879 | 0 / 1
1272 | Al_CircuitFault_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 880 | 0 / 1
1273 | Al_CircuitFault_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 881 | 0 / 1
1274 | Al_CircuitFault_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 882 | 0 / 1
1275 | Al_CircuitFault_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 883 | 0 / 1
1276 | Al_CircuitFault_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 884 | 0 / 1
1277 | Al_CircuitFault_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 885 | 0 / 1
1278 | Al_CircuitFault_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 886 | 0 / 1
1279 | Al_CircuitFault_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 887 | 0 / 1
1280 | Al_CircuitFault_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 888 | 0 / 1
1281 | Al_CircuitFault_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 889 | 0 / 1
1282 | Al_CircuitFault_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 890 | 0 / 1
1283 | Al_CircuitFault_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 891 | 0 / 1
1284 | Al_CircuitFault_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Circuit Fault [0 / 1] | BOOL | Read | Coil | 892 | 0 / 1
1285 | Al_CommErr_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Communication Error [0 / 1] | BOOL | Read | Coil | 893 | 0 / 1
1286 | Al_CommErr_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Communication Error [0 / 1] | BOOL | Read | Coil | 894 | 0 / 1
1287 | Al_CommErr_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Communication Error [0 / 1] | BOOL | Read | Coil | 895 | 0 / 1
1288 | Al_CommErr_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Communication Error [0 / 1] | BOOL | Read | Coil | 896 | 0 / 1
1289 | Al_CommErr_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Communication Error [0 / 1] | BOOL | Read | Coil | 897 | 0 / 1
1290 | Al_CommErr_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Communication Error [0 / 1] | BOOL | Read | Coil | 898 | 0 / 1
1291 | Al_CommErr_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Communication Error [0 / 1] | BOOL | Read | Coil | 899 | 0 / 1
1292 | Al_CommErr_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Communication Error [0 / 1] | BOOL | Read | Coil | 900 | 0 / 1
1293 | Al_CommErr_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Communication Error [0 / 1] | BOOL | Read | Coil | 901 | 0 / 1
1294 | Al_CommErr_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Communication Error [0 / 1] | BOOL | Read | Coil | 902 | 0 / 1
1295 | Al_CommErr_Rotary.Active | AL - Alarm - Rotary - CommUnitation Error [0 / 1] | BOOL | Read | Coil | 903 | 0 / 1
1296 | Al_CommErr_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Communication Error [0 / 1] | BOOL | Read | Coil | 904 | 0 / 1
1297 | Al_CommErr_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Communication Error [0 / 1] | BOOL | Read | Coil | 905 | 0 / 1
1298 | Al_CommErr_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Communication Error [0 / 1] | BOOL | Read | Coil | 906 | 0 / 1
1299 | Al_CommErr_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Communication Error [0 / 1] | BOOL | Read | Coil | 907 | 0 / 1
1300 | Al_CommErr_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Communication Error [0 / 1] | BOOL | Read | Coil | 908 | 0 / 1
1301 | Al_CommErr_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Communication Error [0 / 1] | BOOL | Read | Coil | 909 | 0 / 1
1302 | Al_CommErr_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Communication Error [0 / 1] | BOOL | Read | Coil | 910 | 0 / 1
1303 | Al_CommErr_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Communication Error [0 / 1] | BOOL | Read | Coil | 911 | 0 / 1
1304 | Al_CommErr_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Communication Error [0 / 1] | BOOL | Read | Coil | 912 | 0 / 1
1305 | Al_CommErr_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Communication Error [0 / 1] | BOOL | Read | Coil | 913 | 0 / 1
1306 | Al_Cool.Active | AL - Alarm - Cooling - Device Alarm [0 / 1] | BOOL | Read | Coil | 914 | 0 / 1
1307 | Al_CoolFanFault_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 915 | 0 / 1
1308 | Al_CoolFanFault_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 916 | 0 / 1
1309 | Al_CoolFanFault_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 917 | 0 / 1
1310 | Al_CoolFanFault_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 918 | 0 / 1
1311 | Al_CoolFanFault_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 919 | 0 / 1
1312 | Al_CoolFanFault_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 920 | 0 / 1
1313 | Al_CoolFanFault_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 921 | 0 / 1
1314 | Al_CoolFanFault_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 922 | 0 / 1
1315 | Al_CoolFanFault_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 923 | 0 / 1
1316 | Al_CoolFanFault_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 924 | 0 / 1
1317 | Al_CoolFanFault_Rotary.Active | AL - Alarm - Rotary - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 925 | 0 / 1
1318 | Al_CoolFanFault_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 926 | 0 / 1
1319 | Al_CoolFanFault_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 927 | 0 / 1
1320 | Al_CoolFanFault_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 928 | 0 / 1
1321 | Al_CoolFanFault_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 929 | 0 / 1
1322 | Al_CoolFanFault_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 930 | 0 / 1
1323 | Al_CoolFanFault_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 931 | 0 / 1
1324 | Al_CoolFanFault_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 932 | 0 / 1
1325 | Al_CoolFanFault_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 933 | 0 / 1
1326 | Al_CoolFanFault_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 934 | 0 / 1
1327 | Al_CoolFanFault_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Cooling Fan Fault [0 / 1] | BOOL | Read | Coil | 935 | 0 / 1
1328 | Al_CutOff_ExhFan_1.Active | AL - Alarm - Fan Return 1 - CutOff [0 / 1] | BOOL | Read | Coil | 936 | 0 / 1
1329 | Al_CutOff_ExhFan_10.Active | AL - Alarm - Fan Return 10 - CutOff [0 / 1] | BOOL | Read | Coil | 937 | 0 / 1
1330 | Al_CutOff_ExhFan_2.Active | AL - Alarm - Fan Return 2 - CutOff [0 / 1] | BOOL | Read | Coil | 938 | 0 / 1
1331 | Al_CutOff_ExhFan_3.Active | AL - Alarm - Fan Return 3 - CutOff [0 / 1] | BOOL | Read | Coil | 939 | 0 / 1
1332 | Al_CutOff_ExhFan_4.Active | AL - Alarm - Fan Return 4 - CutOff [0 / 1] | BOOL | Read | Coil | 940 | 0 / 1
1333 | Al_CutOff_ExhFan_5.Active | AL - Alarm - Fan Return 5 - CutOff [0 / 1] | BOOL | Read | Coil | 941 | 0 / 1
1334 | Al_CutOff_ExhFan_6.Active | AL - Alarm - Fan Return 6 - CutOff [0 / 1] | BOOL | Read | Coil | 942 | 0 / 1
1335 | Al_CutOff_ExhFan_7.Active | AL - Alarm - Fan Return 7 - CutOff [0 / 1] | BOOL | Read | Coil | 943 | 0 / 1
1336 | Al_CutOff_ExhFan_8.Active | AL - Alarm - Fan Return 8 - CutOff [0 / 1] | BOOL | Read | Coil | 944 | 0 / 1
1337 | Al_CutOff_ExhFan_9.Active | AL - Alarm - Fan Return 9 - CutOff [0 / 1] | BOOL | Read | Coil | 945 | 0 / 1
1338 | Al_CutOff_Rotary.Active | AL - Alarm - Rotary - CutOff [0 / 1] | BOOL | Read | Coil | 946 | 0 / 1
1339 | Al_CutOff_SupFan_1.Active | AL - Alarm - Fan Supply 1 - CutOff [0 / 1] | BOOL | Read | Coil | 947 | 0 / 1
1340 | Al_CutOff_SupFan_10.Active | AL - Alarm - Fan Supply 10 - CutOff [0 / 1] | BOOL | Read | Coil | 948 | 0 / 1
1341 | Al_CutOff_SupFan_2.Active | AL - Alarm - Fan Supply 2 - CutOff [0 / 1] | BOOL | Read | Coil | 949 | 0 / 1
1342 | Al_CutOff_SupFan_3.Active | AL - Alarm - Fan Supply 3 - CutOff [0 / 1] | BOOL | Read | Coil | 950 | 0 / 1
1343 | Al_CutOff_SupFan_4.Active | AL - Alarm - Fan Supply 4 - CutOff [0 / 1] | BOOL | Read | Coil | 951 | 0 / 1
1344 | Al_CutOff_SupFan_5.Active | AL - Alarm - Fan Supply 5 - CutOff [0 / 1] | BOOL | Read | Coil | 952 | 0 / 1
1345 | Al_CutOff_SupFan_6.Active | AL - Alarm - Fan Supply 6 - CutOff [0 / 1] | BOOL | Read | Coil | 953 | 0 / 1
1346 | Al_CutOff_SupFan_7.Active | AL - Alarm - Fan Supply 7 - CutOff [0 / 1] | BOOL | Read | Coil | 954 | 0 / 1
1347 | Al_CutOff_SupFan_8.Active | AL - Alarm - Fan Supply 8 - CutOff [0 / 1] | BOOL | Read | Coil | 955 | 0 / 1
1348 | Al_CutOff_SupFan_9.Active | AL - Alarm - Fan Supply 9 - CutOff [0 / 1] | BOOL | Read | Coil | 956 | 0 / 1
1349 | Al_DC_Ovld_ExhFan_1.Active | AL - Alarm - Fan Return 1 - DC Over load [0 / 1] | BOOL | Read | Coil | 957 | 0 / 1
1350 | Al_DC_Ovld_ExhFan_10.Active | AL - Alarm - Fan Return 10 - DC Over load [0 / 1] | BOOL | Read | Coil | 958 | 0 / 1
1351 | Al_DC_Ovld_ExhFan_2.Active | AL - Alarm - Fan Return 2 - DC Over load [0 / 1] | BOOL | Read | Coil | 959 | 0 / 1
1352 | Al_DC_Ovld_ExhFan_3.Active | AL - Alarm - Fan Return 3 - DC Over load [0 / 1] | BOOL | Read | Coil | 960 | 0 / 1
1353 | Al_DC_Ovld_ExhFan_4.Active | AL - Alarm - Fan Return 4 - DC Over load [0 / 1] | BOOL | Read | Coil | 961 | 0 / 1
1354 | Al_DC_Ovld_ExhFan_5.Active | AL - Alarm - Fan Return 5 - DC Over load [0 / 1] | BOOL | Read | Coil | 962 | 0 / 1
1355 | Al_DC_Ovld_ExhFan_6.Active | AL - Alarm - Fan Return 6 - DC Over load [0 / 1] | BOOL | Read | Coil | 963 | 0 / 1
1356 | Al_DC_Ovld_ExhFan_7.Active | AL - Alarm - Fan Return 7 - DC Over load [0 / 1] | BOOL | Read | Coil | 964 | 0 / 1
1357 | Al_DC_Ovld_ExhFan_8.Active | AL - Alarm - Fan Return 8 - DC Over load [0 / 1] | BOOL | Read | Coil | 965 | 0 / 1
1358 | Al_DC_Ovld_ExhFan_9.Active | AL - Alarm - Fan Return 9 - DC Over load [0 / 1] | BOOL | Read | Coil | 966 | 0 / 1
1359 | Al_DC_Ovld_Rotary.Active | AL - Alarm - Rotary - DC Overload [0 / 1] | BOOL | Read | Coil | 967 | 0 / 1
1360 | Al_DC_Ovld_SupFan_1.Active | AL - Alarm - Fan Supply 1 - DC Over load [0 / 1] | BOOL | Read | Coil | 968 | 0 / 1
1361 | Al_DC_Ovld_SupFan_10.Active | AL - Alarm - Fan Supply 10 - DC Over load [0 / 1] | BOOL | Read | Coil | 969 | 0 / 1
1362 | Al_DC_Ovld_SupFan_2.Active | AL - Alarm - Fan Supply 2 - DC Over load [0 / 1] | BOOL | Read | Coil | 970 | 0 / 1
1363 | Al_DC_Ovld_SupFan_3.Active | AL - Alarm - Fan Supply 3 - DC Over load [0 / 1] | BOOL | Read | Coil | 971 | 0 / 1
1364 | Al_DC_Ovld_SupFan_4.Active | AL - Alarm - Fan Supply 4 - DC Over load [0 / 1] | BOOL | Read | Coil | 972 | 0 / 1
1365 | Al_DC_Ovld_SupFan_5.Active | AL - Alarm - Fan Supply 5 - DC Over load [0 / 1] | BOOL | Read | Coil | 973 | 0 / 1
1366 | Al_DC_Ovld_SupFan_6.Active | AL - Alarm - Fan Supply 6 - DC Over load [0 / 1] | BOOL | Read | Coil | 974 | 0 / 1
1367 | Al_DC_Ovld_SupFan_7.Active | AL - Alarm - Fan Supply 7 - DC Over load [0 / 1] | BOOL | Read | Coil | 975 | 0 / 1
1368 | Al_DC_Ovld_SupFan_8.Active | AL - Alarm - Fan Supply 8 - DC Over load [0 / 1] | BOOL | Read | Coil | 976 | 0 / 1
1369 | Al_DC_Ovld_SupFan_9.Active | AL - Alarm - Fan Supply 9 - DC Over load [0 / 1] | BOOL | Read | Coil | 977 | 0 / 1
1370 | Al_ElectTherm_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 978 | 0 / 1
1371 | Al_ElectTherm_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 979 | 0 / 1
1372 | Al_ElectTherm_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 980 | 0 / 1
1373 | Al_ElectTherm_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 981 | 0 / 1
1374 | Al_ElectTherm_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 982 | 0 / 1
1375 | Al_ElectTherm_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 983 | 0 / 1
1376 | Al_ElectTherm_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 984 | 0 / 1
1377 | Al_ElectTherm_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 985 | 0 / 1
1378 | Al_ElectTherm_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 986 | 0 / 1
1379 | Al_ElectTherm_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 987 | 0 / 1
1380 | Al_ElectTherm_Rotary.Active | AL - Alarm - Rotary - Electric Thermal [0 / 1] | BOOL | Read | Coil | 988 | 0 / 1
1381 | Al_ElectTherm_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 989 | 0 / 1
1382 | Al_ElectTherm_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 990 | 0 / 1
1383 | Al_ElectTherm_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 991 | 0 / 1
1384 | Al_ElectTherm_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 992 | 0 / 1
1385 | Al_ElectTherm_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 993 | 0 / 1
1386 | Al_ElectTherm_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 994 | 0 / 1
1387 | Al_ElectTherm_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 995 | 0 / 1
1388 | Al_ElectTherm_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 996 | 0 / 1
1389 | Al_ElectTherm_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 997 | 0 / 1
1390 | Al_ElectTherm_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Electric Thermal [0 / 1] | BOOL | Read | Coil | 998 | 0 / 1
1391 | Al_Err_retain_write.Active | AL - Alarm - Error retain write [0 / 1] | BOOL | Read | Coil | 999 | 0 / 1
1392 | Al_ExhTempPrb.Active | AL - Alarm - Probe - Temperature Exhaust [0 / 1] | BOOL | Read | Coil | 1000 | 0 / 1
1393 | Al_ExtFaultA_ExhFan_1.Active | AL - Alarm - Fan Return 1 - External Fault A [0 / 1] | BOOL | Read | Coil | 1001 | 0 / 1
1394 | Al_ExtFaultA_ExhFan_10.Active | AL - Alarm - Fan Return 10 - External Fault A [0 / 1] | BOOL | Read | Coil | 1002 | 0 / 1
1395 | Al_ExtFaultA_ExhFan_2.Active | AL - Alarm - Fan Return 2 - External Fault A [0 / 1] | BOOL | Read | Coil | 1003 | 0 / 1
1396 | Al_ExtFaultA_ExhFan_3.Active | AL - Alarm - Fan Return 3 - External Fault A [0 / 1] | BOOL | Read | Coil | 1004 | 0 / 1
1397 | Al_ExtFaultA_ExhFan_4.Active | AL - Alarm - Fan Return 4 - External Fault A [0 / 1] | BOOL | Read | Coil | 1005 | 0 / 1
1398 | Al_ExtFaultA_ExhFan_5.Active | AL - Alarm - Fan Return 5 - External Fault A [0 / 1] | BOOL | Read | Coil | 1006 | 0 / 1
1399 | Al_ExtFaultA_ExhFan_6.Active | AL - Alarm - Fan Return 6 - External Fault A [0 / 1] | BOOL | Read | Coil | 1007 | 0 / 1
1400 | Al_ExtFaultA_ExhFan_7.Active | AL - Alarm - Fan Return 7 - External Fault A [0 / 1] | BOOL | Read | Coil | 1008 | 0 / 1
1401 | Al_ExtFaultA_ExhFan_8.Active | AL - Alarm - Fan Return 8 - External Fault A [0 / 1] | BOOL | Read | Coil | 1009 | 0 / 1
1402 | Al_ExtFaultA_ExhFan_9.Active | AL - Alarm - Fan Return 9 - External Fault A [0 / 1] | BOOL | Read | Coil | 1010 | 0 / 1
1403 | Al_ExtFaultA_Rotary.Active | AL - Alarm - Rotary - External Fault A [0 / 1] | BOOL | Read | Coil | 1011 | 0 / 1
1404 | Al_ExtFaultA_SupFan_1.Active | AL - Alarm - Fan Supply 1 - External Fault A [0 / 1] | BOOL | Read | Coil | 1012 | 0 / 1
1405 | Al_ExtFaultA_SupFan_10.Active | AL - Alarm - Fan Supply 10 - External Fault A [0 / 1] | BOOL | Read | Coil | 1013 | 0 / 1
1406 | Al_ExtFaultA_SupFan_2.Active | AL - Alarm - Fan Supply 2 - External Fault A [0 / 1] | BOOL | Read | Coil | 1014 | 0 / 1
1407 | Al_ExtFaultA_SupFan_3.Active | AL - Alarm - Fan Supply 3 - External Fault A [0 / 1] | BOOL | Read | Coil | 1015 | 0 / 1
1408 | Al_ExtFaultA_SupFan_4.Active | AL - Alarm - Fan Supply 4 - External Fault A [0 / 1] | BOOL | Read | Coil | 1016 | 0 / 1
1409 | Al_ExtFaultA_SupFan_5.Active | AL - Alarm - Fan Supply 5 - External Fault A [0 / 1] | BOOL | Read | Coil | 1017 | 0 / 1
1410 | Al_ExtFaultA_SupFan_6.Active | AL - Alarm - Fan Supply 6 - External Fault A [0 / 1] | BOOL | Read | Coil | 1018 | 0 / 1
1411 | Al_ExtFaultA_SupFan_7.Active | AL - Alarm - Fan Supply 7 - External Fault A [0 / 1] | BOOL | Read | Coil | 1019 | 0 / 1
1412 | Al_ExtFaultA_SupFan_8.Active | AL - Alarm - Fan Supply 8 - External Fault A [0 / 1] | BOOL | Read | Coil | 1020 | 0 / 1
1413 | Al_ExtFaultA_SupFan_9.Active | AL - Alarm - Fan Supply 9 - External Fault A [0 / 1] | BOOL | Read | Coil | 1021 | 0 / 1
1414 | Al_ExtFaultB_ExhFan_1.Active | AL - Alarm - Fan Return 1 - External Fault B [0 / 1] | BOOL | Read | Coil | 1022 | 0 / 1
1415 | Al_ExtFaultB_ExhFan_10.Active | AL - Alarm - Fan Return 10 - External Fault B [0 / 1] | BOOL | Read | Coil | 1023 | 0 / 1
1416 | Al_ExtFaultB_ExhFan_2.Active | AL - Alarm - Fan Return 2 - External Fault B [0 / 1] | BOOL | Read | Coil | 1024 | 0 / 1
1417 | Al_ExtFaultB_ExhFan_3.Active | AL - Alarm - Fan Return 3 - External Fault B [0 / 1] | BOOL | Read | Coil | 1025 | 0 / 1
1418 | Al_ExtFaultB_ExhFan_4.Active | AL - Alarm - Fan Return 4 - External Fault B [0 / 1] | BOOL | Read | Coil | 1026 | 0 / 1
1419 | Al_ExtFaultB_ExhFan_5.Active | AL - Alarm - Fan Return 5 - External Fault B [0 / 1] | BOOL | Read | Coil | 1027 | 0 / 1
1420 | Al_ExtFaultB_ExhFan_6.Active | AL - Alarm - Fan Return 6 - External Fault B [0 / 1] | BOOL | Read | Coil | 1028 | 0 / 1
1421 | Al_ExtFaultB_ExhFan_7.Active | AL - Alarm - Fan Return 7 - External Fault B [0 / 1] | BOOL | Read | Coil | 1029 | 0 / 1
1422 | Al_ExtFaultB_ExhFan_8.Active | AL - Alarm - Fan Return 8 - External Fault B [0 / 1] | BOOL | Read | Coil | 1030 | 0 / 1
1423 | Al_ExtFaultB_ExhFan_9.Active | AL - Alarm - Fan Return 9 - External Fault B [0 / 1] | BOOL | Read | Coil | 1031 | 0 / 1
1424 | Al_ExtFaultB_Rotary.Active | AL - Alarm - Rotary - External Fault B [0 / 1] | BOOL | Read | Coil | 1032 | 0 / 1
1425 | Al_ExtFaultB_SupFan_1.Active | AL - Alarm - Fan Supply 1 - External Fault B [0 / 1] | BOOL | Read | Coil | 1033 | 0 / 1
1426 | Al_ExtFaultB_SupFan_10.Active | AL - Alarm - Fan Supply 10 - External Fault B [0 / 1] | BOOL | Read | Coil | 1034 | 0 / 1
1427 | Al_ExtFaultB_SupFan_2.Active | AL - Alarm - Fan Supply 2 - External Fault B [0 / 1] | BOOL | Read | Coil | 1035 | 0 / 1
1428 | Al_ExtFaultB_SupFan_3.Active | AL - Alarm - Fan Supply 3 - External Fault B [0 / 1] | BOOL | Read | Coil | 1036 | 0 / 1
1429 | Al_ExtFaultB_SupFan_4.Active | AL - Alarm - Fan Supply 4 - External Fault B [0 / 1] | BOOL | Read | Coil | 1037 | 0 / 1
1430 | Al_ExtFaultB_SupFan_5.Active | AL - Alarm - Fan Supply 5 - External Fault B [0 / 1] | BOOL | Read | Coil | 1038 | 0 / 1
1431 | Al_ExtFaultB_SupFan_6.Active | AL - Alarm - Fan Supply 6 - External Fault B [0 / 1] | BOOL | Read | Coil | 1039 | 0 / 1
1432 | Al_ExtFaultB_SupFan_7.Active | AL - Alarm - Fan Supply 7 - External Fault B [0 / 1] | BOOL | Read | Coil | 1040 | 0 / 1
1433 | Al_ExtFaultB_SupFan_8.Active | AL - Alarm - Fan Supply 8 - External Fault B [0 / 1] | BOOL | Read | Coil | 1041 | 0 / 1
1434 | Al_ExtFaultB_SupFan_9.Active | AL - Alarm - Fan Supply 9 - External Fault B [0 / 1] | BOOL | Read | Coil | 1042 | 0 / 1
1435 | Al_ExtTempPrb.Active | AL - Alarm - Probe - Temperature External [0 / 1] | BOOL | Read | Coil | 1043 | 0 / 1
1436 | Al_Fire.Active | AL - Alarm - Fire [0 / 1] | BOOL | Read | Coil | 1044 | 0 / 1
1437 | Al_FireExh.Active | AL - Alarm - Fire - Return Temperature [0 / 1] | BOOL | Read | Coil | 1045 | 0 / 1
1438 | Al_GroundFault_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1046 | 0 / 1
1439 | Al_GroundFault_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1047 | 0 / 1
1440 | Al_GroundFault_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1048 | 0 / 1
1441 | Al_GroundFault_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1049 | 0 / 1
1442 | Al_GroundFault_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1050 | 0 / 1
1443 | Al_GroundFault_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1051 | 0 / 1
1444 | Al_GroundFault_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1052 | 0 / 1
1445 | Al_GroundFault_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1053 | 0 / 1
1446 | Al_GroundFault_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1054 | 0 / 1
1447 | Al_GroundFault_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1055 | 0 / 1
1448 | Al_GroundFault_Rotary.Active | AL - Alarm - Rotary - Ground Fault [0 / 1] | BOOL | Read | Coil | 1056 | 0 / 1
1449 | Al_GroundFault_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1057 | 0 / 1
1450 | Al_GroundFault_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1058 | 0 / 1
1451 | Al_GroundFault_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1059 | 0 / 1
1452 | Al_GroundFault_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1060 | 0 / 1
1453 | Al_GroundFault_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1061 | 0 / 1
1454 | Al_GroundFault_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1062 | 0 / 1
1455 | Al_GroundFault_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1063 | 0 / 1
1456 | Al_GroundFault_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1064 | 0 / 1
1457 | Al_GroundFault_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1065 | 0 / 1
1458 | Al_GroundFault_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Ground Fault [0 / 1] | BOOL | Read | Coil | 1066 | 0 / 1
1459 | Al_Heat.Active | AL - Alarm - Heating - Device Alarm [0 / 1] | BOOL | Read | Coil | 1067 | 0 / 1
1460 | Al_HeatCoilTempPrb.Active | AL - Alarm - Probe - Temperature Water Heating coil [0 / 1] | BOOL | Read | Coil | 1068 | 0 / 1
1461 | Al_HeatExchgWorkHrsWarn.Active | AL - Alarm - HeatExchanger - HeatExchanger Works Hour Warning [0 / 1] | BOOL | Read | Coil | 1069 | 0 / 1
1462 | Al_HeatSink_ExhFan_1.Active | AL - Alarm - Fan Return 1 - HeatSink [0 / 1] | BOOL | Read | Coil | 1070 | 0 / 1
1463 | Al_HeatSink_ExhFan_10.Active | AL - Alarm - Fan Return 10 - HeatSink [0 / 1] | BOOL | Read | Coil | 1071 | 0 / 1
1464 | Al_HeatSink_ExhFan_2.Active | AL - Alarm - Fan Return 2 - HeatSink [0 / 1] | BOOL | Read | Coil | 1072 | 0 / 1
1465 | Al_HeatSink_ExhFan_3.Active | AL - Alarm - Fan Return 3 - HeatSink [0 / 1] | BOOL | Read | Coil | 1073 | 0 / 1
1466 | Al_HeatSink_ExhFan_4.Active | AL - Alarm - Fan Return 4 - HeatSink [0 / 1] | BOOL | Read | Coil | 1074 | 0 / 1
1467 | Al_HeatSink_ExhFan_5.Active | AL - Alarm - Fan Return 5 - HeatSink [0 / 1] | BOOL | Read | Coil | 1075 | 0 / 1
1468 | Al_HeatSink_ExhFan_6.Active | AL - Alarm - Fan Return 6 - HeatSink [0 / 1] | BOOL | Read | Coil | 1076 | 0 / 1
1469 | Al_HeatSink_ExhFan_7.Active | AL - Alarm - Fan Return 7 - HeatSink [0 / 1] | BOOL | Read | Coil | 1077 | 0 / 1
1470 | Al_HeatSink_ExhFan_8.Active | AL - Alarm - Fan Return 8 - HeatSink [0 / 1] | BOOL | Read | Coil | 1078 | 0 / 1
1471 | Al_HeatSink_ExhFan_9.Active | AL - Alarm - Fan Return 9 - HeatSink [0 / 1] | BOOL | Read | Coil | 1079 | 0 / 1
1472 | Al_HeatSink_Rotary.Active | AL - Alarm - Rotary - HeatSink [0 / 1] | BOOL | Read | Coil | 1080 | 0 / 1
1473 | Al_HeatSink_SupFan_1.Active | AL - Alarm - Fan Supply 1 - HeatSink [0 / 1] | BOOL | Read | Coil | 1081 | 0 / 1
1474 | Al_HeatSink_SupFan_10.Active | AL - Alarm - Fan Supply 10 - HeatSink [0 / 1] | BOOL | Read | Coil | 1082 | 0 / 1
1475 | Al_HeatSink_SupFan_2.Active | AL - Alarm - Fan Supply 2 - HeatSink [0 / 1] | BOOL | Read | Coil | 1083 | 0 / 1
1476 | Al_HeatSink_SupFan_3.Active | AL - Alarm - Fan Supply 3 - HeatSink [0 / 1] | BOOL | Read | Coil | 1084 | 0 / 1
1477 | Al_HeatSink_SupFan_4.Active | AL - Alarm - Fan Supply 4 - HeatSink [0 / 1] | BOOL | Read | Coil | 1085 | 0 / 1
1478 | Al_HeatSink_SupFan_5.Active | AL - Alarm - Fan Supply 5 - HeatSink [0 / 1] | BOOL | Read | Coil | 1086 | 0 / 1
1479 | Al_HeatSink_SupFan_6.Active | AL - Alarm - Fan Supply 6 - HeatSink [0 / 1] | BOOL | Read | Coil | 1087 | 0 / 1
1480 | Al_HeatSink_SupFan_7.Active | AL - Alarm - Fan Supply 7 - HeatSink [0 / 1] | BOOL | Read | Coil | 1088 | 0 / 1
1481 | Al_HeatSink_SupFan_8.Active | AL - Alarm - Fan Supply 8 - HeatSink [0 / 1] | BOOL | Read | Coil | 1089 | 0 / 1
1482 | Al_HeatSink_SupFan_9.Active | AL - Alarm - Fan Supply 9 - HeatSink [0 / 1] | BOOL | Read | Coil | 1090 | 0 / 1
1483 | AL_Hot_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Hot [0 / 1] | BOOL | Read | Coil | 1091 | 0 / 1
1484 | AL_Hot_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Hot [0 / 1] | BOOL | Read | Coil | 1092 | 0 / 1
1485 | AL_Hot_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Hot [0 / 1] | BOOL | Read | Coil | 1093 | 0 / 1
1486 | AL_Hot_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Hot [0 / 1] | BOOL | Read | Coil | 1094 | 0 / 1
1487 | AL_Hot_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Hot [0 / 1] | BOOL | Read | Coil | 1095 | 0 / 1
1488 | AL_Hot_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Hot [0 / 1] | BOOL | Read | Coil | 1096 | 0 / 1
1489 | AL_Hot_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Hot [0 / 1] | BOOL | Read | Coil | 1097 | 0 / 1
1490 | AL_Hot_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Hot [0 / 1] | BOOL | Read | Coil | 1098 | 0 / 1
1491 | AL_Hot_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Hot [0 / 1] | BOOL | Read | Coil | 1099 | 0 / 1
1492 | AL_Hot_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Hot [0 / 1] | BOOL | Read | Coil | 1100 | 0 / 1
1493 | AL_Hot_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Hot [0 / 1] | BOOL | Read | Coil | 1101 | 0 / 1
1494 | AL_Hot_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Hot [0 / 1] | BOOL | Read | Coil | 1102 | 0 / 1
1495 | AL_Hot_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Hot [0 / 1] | BOOL | Read | Coil | 1103 | 0 / 1
1496 | AL_Hot_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Hot [0 / 1] | BOOL | Read | Coil | 1104 | 0 / 1
1497 | AL_Hot_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Hot [0 / 1] | BOOL | Read | Coil | 1105 | 0 / 1
1498 | AL_Hot_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Hot [0 / 1] | BOOL | Read | Coil | 1106 | 0 / 1
1499 | AL_Hot_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Hot [0 / 1] | BOOL | Read | Coil | 1107 | 0 / 1
1500 | AL_Hot_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Hot [0 / 1] | BOOL | Read | Coil | 1108 | 0 / 1
1501 | AL_Hot_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Hot [0 / 1] | BOOL | Read | Coil | 1109 | 0 / 1
1502 | AL_Hot_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Hot [0 / 1] | BOOL | Read | Coil | 1110 | 0 / 1
1503 | Al_Hum.Active | AL - Alarm - Humidifier [0 / 1] | BOOL | Read | Coil | 1111 | 0 / 1
1504 | Al_HumWorkHrsWarn.Active | AL - Alarm - Humidity - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 1112 | 0 / 1
1505 | Al_HW_Fault_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1113 | 0 / 1
1506 | Al_HW_Fault_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1114 | 0 / 1
1507 | Al_HW_Fault_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1115 | 0 / 1
1508 | Al_HW_Fault_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1116 | 0 / 1
1509 | Al_HW_Fault_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1117 | 0 / 1
1510 | Al_HW_Fault_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1118 | 0 / 1
1511 | Al_HW_Fault_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1119 | 0 / 1
1512 | Al_HW_Fault_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1120 | 0 / 1
1513 | Al_HW_Fault_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1121 | 0 / 1
1514 | Al_HW_Fault_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1122 | 0 / 1
1515 | Al_HW_Fault_Rotary.Active | AL - Alarm - Rotary - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1123 | 0 / 1
1516 | Al_HW_Fault_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1124 | 0 / 1
1517 | Al_HW_Fault_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1125 | 0 / 1
1518 | Al_HW_Fault_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1126 | 0 / 1
1519 | Al_HW_Fault_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1127 | 0 / 1
1520 | Al_HW_Fault_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1128 | 0 / 1
1521 | Al_HW_Fault_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1129 | 0 / 1
1522 | Al_HW_Fault_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1130 | 0 / 1
1523 | Al_HW_Fault_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1131 | 0 / 1
1524 | Al_HW_Fault_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1132 | 0 / 1
1525 | Al_HW_Fault_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Hardware Fault [0 / 1] | BOOL | Read | Coil | 1133 | 0 / 1
1526 | Al_I2RIGBTFault_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1134 | 0 / 1
1527 | Al_I2RIGBTFault_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1135 | 0 / 1
1528 | Al_I2RIGBTFault_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1136 | 0 / 1
1529 | Al_I2RIGBTFault_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1137 | 0 / 1
1530 | Al_I2RIGBTFault_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1138 | 0 / 1
1531 | Al_I2RIGBTFault_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1139 | 0 / 1
1532 | Al_I2RIGBTFault_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1140 | 0 / 1
1533 | Al_I2RIGBTFault_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1141 | 0 / 1
1534 | Al_I2RIGBTFault_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1142 | 0 / 1
1535 | Al_I2RIGBTFault_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1143 | 0 / 1
1536 | Al_I2RIGBTFault_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1144 | 0 / 1
1537 | Al_I2RIGBTFault_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1145 | 0 / 1
1538 | Al_I2RIGBTFault_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1146 | 0 / 1
1539 | Al_I2RIGBTFault_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1147 | 0 / 1
1540 | Al_I2RIGBTFault_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1148 | 0 / 1
1541 | Al_I2RIGBTFault_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1149 | 0 / 1
1542 | Al_I2RIGBTFault_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1150 | 0 / 1
1543 | Al_I2RIGBTFault_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1151 | 0 / 1
1544 | Al_I2RIGBTFault_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1152 | 0 / 1
1545 | Al_I2RIGBTFault_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - I2RIGBT Fault [0 / 1] | BOOL | Read | Coil | 1153 | 0 / 1
1546 | AL_IGBTOvercurrent_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1154 | 0 / 1
1547 | AL_IGBTOvercurrent_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1155 | 0 / 1
1548 | AL_IGBTOvercurrent_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1156 | 0 / 1
1549 | AL_IGBTOvercurrent_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1157 | 0 / 1
1550 | AL_IGBTOvercurrent_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1158 | 0 / 1
1551 | AL_IGBTOvercurrent_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1159 | 0 / 1
1552 | AL_IGBTOvercurrent_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1160 | 0 / 1
1553 | AL_IGBTOvercurrent_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1161 | 0 / 1
1554 | AL_IGBTOvercurrent_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1162 | 0 / 1
1555 | AL_IGBTOvercurrent_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1163 | 0 / 1
1556 | AL_IGBTOvercurrent_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1164 | 0 / 1
1557 | AL_IGBTOvercurrent_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1165 | 0 / 1
1558 | AL_IGBTOvercurrent_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1166 | 0 / 1
1559 | AL_IGBTOvercurrent_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1167 | 0 / 1
1560 | AL_IGBTOvercurrent_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1168 | 0 / 1
1561 | AL_IGBTOvercurrent_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1169 | 0 / 1
1562 | AL_IGBTOvercurrent_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1170 | 0 / 1
1563 | AL_IGBTOvercurrent_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1171 | 0 / 1
1564 | AL_IGBTOvercurrent_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1172 | 0 / 1
1565 | AL_IGBTOvercurrent_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - IGBT Over current [0 / 1] | BOOL | Read | Coil | 1173 | 0 / 1
1566 | Al_InvOverheat_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1174 | 0 / 1
1567 | Al_InvOverheat_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1175 | 0 / 1
1568 | Al_InvOverheat_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1176 | 0 / 1
1569 | Al_InvOverheat_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1177 | 0 / 1
1570 | Al_InvOverheat_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1178 | 0 / 1
1571 | Al_InvOverheat_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1179 | 0 / 1
1572 | Al_InvOverheat_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1180 | 0 / 1
1573 | Al_InvOverheat_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1181 | 0 / 1
1574 | Al_InvOverheat_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1182 | 0 / 1
1575 | Al_InvOverheat_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1183 | 0 / 1
1576 | Al_InvOverheat_Rotary.Active | AL - Alarm - Rotary - Inverter OverHeat [0 / 1] | BOOL | Read | Coil | 1184 | 0 / 1
1577 | Al_InvOverheat_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1185 | 0 / 1
1578 | Al_InvOverheat_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1186 | 0 / 1
1579 | Al_InvOverheat_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1187 | 0 / 1
1580 | Al_InvOverheat_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1188 | 0 / 1
1581 | Al_InvOverheat_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1189 | 0 / 1
1582 | Al_InvOverheat_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1190 | 0 / 1
1583 | Al_InvOverheat_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1191 | 0 / 1
1584 | Al_InvOverheat_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1192 | 0 / 1
1585 | Al_InvOverheat_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1193 | 0 / 1
1586 | Al_InvOverheat_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Inverter Over Heat [0 / 1] | BOOL | Read | Coil | 1194 | 0 / 1
1587 | Al_InvOvld_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1195 | 0 / 1
1588 | Al_InvOvld_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1196 | 0 / 1
1589 | Al_InvOvld_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1197 | 0 / 1
1590 | Al_InvOvld_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1198 | 0 / 1
1591 | Al_InvOvld_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1199 | 0 / 1
1592 | Al_InvOvld_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1200 | 0 / 1
1593 | Al_InvOvld_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1201 | 0 / 1
1594 | Al_InvOvld_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1202 | 0 / 1
1595 | Al_InvOvld_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1203 | 0 / 1
1596 | Al_InvOvld_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1204 | 0 / 1
1597 | Al_InvOvld_Rotary.Active | AL - Alarm - Rotary - Inverter OverLoad [0 / 1] | BOOL | Read | Coil | 1205 | 0 / 1
1598 | Al_InvOvld_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1206 | 0 / 1
1599 | Al_InvOvld_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1207 | 0 / 1
1600 | Al_InvOvld_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1208 | 0 / 1
1601 | Al_InvOvld_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1209 | 0 / 1
1602 | Al_InvOvld_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1210 | 0 / 1
1603 | Al_InvOvld_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1211 | 0 / 1
1604 | Al_InvOvld_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1212 | 0 / 1
1605 | Al_InvOvld_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1213 | 0 / 1
1606 | Al_InvOvld_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1214 | 0 / 1
1607 | Al_InvOvld_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Inverter Over Load [0 / 1] | BOOL | Read | Coil | 1215 | 0 / 1
1608 | Al_LowSupplyTemp.Active | AL - Alarm - Probe - Low Supply Temperature [0 / 1] | BOOL | Read | Coil | 1216 | 0 / 1
1609 | Al_LowVolt_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1217 | 0 / 1
1610 | Al_LowVolt_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1218 | 0 / 1
1611 | Al_LowVolt_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1219 | 0 / 1
1612 | Al_LowVolt_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1220 | 0 / 1
1613 | Al_LowVolt_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1221 | 0 / 1
1614 | Al_LowVolt_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1222 | 0 / 1
1615 | Al_LowVolt_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1223 | 0 / 1
1616 | Al_LowVolt_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1224 | 0 / 1
1617 | Al_LowVolt_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1225 | 0 / 1
1618 | Al_LowVolt_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1226 | 0 / 1
1619 | Al_LowVolt_Rotary.Active | AL - Alarm - Rotary - Low Voltage [0 / 1] | BOOL | Read | Coil | 1227 | 0 / 1
1620 | Al_LowVolt_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1228 | 0 / 1
1621 | Al_LowVolt_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1229 | 0 / 1
1622 | Al_LowVolt_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1230 | 0 / 1
1623 | Al_LowVolt_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1231 | 0 / 1
1624 | Al_LowVolt_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1232 | 0 / 1
1625 | Al_LowVolt_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1233 | 0 / 1
1626 | Al_LowVolt_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1234 | 0 / 1
1627 | Al_LowVolt_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1235 | 0 / 1
1628 | Al_LowVolt_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1236 | 0 / 1
1629 | Al_LowVolt_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Low Voltage [0 / 1] | BOOL | Read | Coil | 1237 | 0 / 1
1630 | Al_MB_AO1.Active | AL - Alarm - Control Circuit - AO1 [0 / 1] | BOOL | Read | Coil | 1238 | 0 / 1
1631 | Al_MB_AO1_AO4_PWM.Active | AL - Alarm - Control Circuit - AO1_AO4_PWM [0 / 1] | BOOL | Read | Coil | 1239 | 0 / 1
1632 | Al_MB_AO2.Active | AL - Alarm - Control Circuit - AO2 [0 / 1] | BOOL | Read | Coil | 1240 | 0 / 1
1633 | Al_MB_AO3.Active | AL - Alarm - Control Circuit - AO3 [0 / 1] | BOOL | Read | Coil | 1241 | 0 / 1
1634 | Al_MB_AO4.Active | AL - Alarm - Control Circuit - AO4 [0 / 1] | BOOL | Read | Coil | 1242 | 0 / 1
1635 | Al_MB_Control_Supply.Active | AL - Alarm - Control Circuit - Control_Supply [0 / 1] | BOOL | Read | Coil | 1243 | 0 / 1
1636 | Al_MB_Control_Temp.Active | AL - Alarm - Control Circuit - Control_Temp [0 / 1] | BOOL | Read | Coil | 1244 | 0 / 1
1637 | Al_MB_Humidity.Active | AL - Alarm - Control Circuit - Humidity [0 / 1] | BOOL | Read | Coil | 1245 | 0 / 1
1638 | Al_MB_Press_Fan_Return.Active | AL - Alarm - Control Circuit - Press_Fan_Return [0 / 1] | BOOL | Read | Coil | 1246 | 0 / 1
1639 | Al_MB_Press_Fan_Supply.Active | AL - Alarm - Control Circuit - Press_Fan_Supply [0 / 1] | BOOL | Read | Coil | 1247 | 0 / 1
1640 | Al_MB_Press_Filter_Return.Active | AL - Alarm - Control Circuit - Press_Filter_Return [0 / 1] | BOOL | Read | Coil | 1248 | 0 / 1
1641 | Al_MB_Press_Filter_Supply.Active | AL - Alarm - Control Circuit - Press_Filter_Supply [0 / 1] | BOOL | Read | Coil | 1249 | 0 / 1
1642 | Al_MB_Supply24.Active | AL - Alarm - Control Circuit - Supply24 [0 / 1] | BOOL | Read | Coil | 1250 | 0 / 1
1643 | Al_MB_Temp_Fan_Return.Active | AL - Alarm - Control Circuit - Temp_Fan_Return [0 / 1] | BOOL | Read | Coil | 1251 | 0 / 1
1644 | Al_MB_Temp_Fan_Supply.Active | AL - Alarm - Control Circuit - Temp_Fan_Supply [0 / 1] | BOOL | Read | Coil | 1252 | 0 / 1
1645 | Al_MB_Temp_Filter_Return.Active | AL - Alarm - Control Circuit - Temp_Filter_Return [0 / 1] | BOOL | Read | Coil | 1253 | 0 / 1
1646 | Al_MB_Temp_Filter_Supply.Active | AL - Alarm - Control Circuit - Temp_Filter_Supply [0 / 1] | BOOL | Read | Coil | 1254 | 0 / 1
1647 | Al_MB_Temperature.Active | AL - Alarm - Control Circuit - Temperature [0 / 1] | BOOL | Read | Coil | 1255 | 0 / 1
1648 | Al_MotorFault_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1256 | 0 / 1
1649 | Al_MotorFault_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1257 | 0 / 1
1650 | Al_MotorFault_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1258 | 0 / 1
1651 | Al_MotorFault_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1259 | 0 / 1
1652 | Al_MotorFault_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1260 | 0 / 1
1653 | Al_MotorFault_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1261 | 0 / 1
1654 | Al_MotorFault_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1262 | 0 / 1
1655 | Al_MotorFault_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1263 | 0 / 1
1656 | Al_MotorFault_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1264 | 0 / 1
1657 | Al_MotorFault_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1265 | 0 / 1
1658 | Al_MotorFault_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1266 | 0 / 1
1659 | Al_MotorFault_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1267 | 0 / 1
1660 | Al_MotorFault_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1268 | 0 / 1
1661 | Al_MotorFault_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1269 | 0 / 1
1662 | Al_MotorFault_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1270 | 0 / 1
1663 | Al_MotorFault_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1271 | 0 / 1
1664 | Al_MotorFault_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1272 | 0 / 1
1665 | Al_MotorFault_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1273 | 0 / 1
1666 | Al_MotorFault_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1274 | 0 / 1
1667 | Al_MotorOverheat_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1275 | 0 / 1
1668 | Al_MotorOverheat_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1276 | 0 / 1
1669 | Al_MotorOverheat_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1277 | 0 / 1
1670 | Al_MotorOverheat_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1278 | 0 / 1
1671 | Al_MotorOverheat_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1279 | 0 / 1
1672 | Al_MotorOverheat_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1280 | 0 / 1
1673 | Al_MotorOverheat_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1281 | 0 / 1
1674 | Al_MotorOverheat_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1282 | 0 / 1
1675 | Al_MotorOverheat_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1283 | 0 / 1
1676 | Al_MotorOverheat_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1284 | 0 / 1
1677 | Al_MotorOverheat_Rotary.Active | AL - Alarm - Rotary - Motor Overheat [0 / 1] | BOOL | Read | Coil | 1285 | 0 / 1
1678 | Al_MotorOverheat_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1286 | 0 / 1
1679 | Al_MotorOverheat_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1287 | 0 / 1
1680 | Al_MotorOverheat_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1288 | 0 / 1
1681 | Al_MotorOverheat_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1289 | 0 / 1
1682 | Al_MotorOverheat_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1290 | 0 / 1
1683 | Al_MotorOverheat_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1291 | 0 / 1
1684 | Al_MotorOverheat_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1292 | 0 / 1
1685 | Al_MotorOverheat_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1293 | 0 / 1
1686 | Al_MotorOverheat_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1294 | 0 / 1
1687 | Al_MotorOverheat_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Motor Over heat [0 / 1] | BOOL | Read | Coil | 1295 | 0 / 1
1688 | Al_Offline_cpCOe.Active | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | BOOL | Read | Coil | 1296 | 0 / 1
1689 | Al_Offline_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Offline [0 / 1] | BOOL | Read | Coil | 1297 | 0 / 1
1690 | Al_Offline_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Offline [0 / 1] | BOOL | Read | Coil | 1298 | 0 / 1
1691 | Al_Offline_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Offline [0 / 1] | BOOL | Read | Coil | 1299 | 0 / 1
1692 | Al_Offline_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Offline [0 / 1] | BOOL | Read | Coil | 1300 | 0 / 1
1693 | Al_Offline_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Offline [0 / 1] | BOOL | Read | Coil | 1301 | 0 / 1
1694 | Al_Offline_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Offline [0 / 1] | BOOL | Read | Coil | 1302 | 0 / 1
1695 | Al_Offline_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Offline [0 / 1] | BOOL | Read | Coil | 1303 | 0 / 1
1696 | Al_Offline_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Offline [0 / 1] | BOOL | Read | Coil | 1304 | 0 / 1
1697 | Al_Offline_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Offline [0 / 1] | BOOL | Read | Coil | 1305 | 0 / 1
1698 | Al_Offline_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Offline [0 / 1] | BOOL | Read | Coil | 1306 | 0 / 1
1699 | Al_Offline_MainBoard.Active | AL - Alarm - Control Circuit - Offline [0 / 1] | BOOL | Read | Coil | 1307 | 0 / 1
1700 | Al_Offline_Rotary.Active | AL - Alarm - Rotary - Offline [0 / 1] | BOOL | Read | Coil | 1308 | 0 / 1
1701 | Al_Offline_SP_ExhHum.Active | AL - Alarm - Probe - Return Humidity - Offline [0 / 1] | BOOL | Read | Coil | 1309 | 0 / 1
1702 | Al_Offline_SP_ExhPress.Active | AL - Alarm - Probe - Return Air Pressure - Offline [0 / 1] | BOOL | Read | Coil | 1310 | 0 / 1
1703 | Al_Offline_SP_SupplyHum.Active | AL - Alarm - Probe - Supply humidity - Offline [0 / 1] | BOOL | Read | Coil | 1311 | 0 / 1
1704 | Al_Offline_SP_SupplyPress.Active | AL - Alarm - Probe - Supply Air Pressure - Offline [0 / 1] | BOOL | Read | Coil | 1312 | 0 / 1
1705 | Al_Offline_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Offline [0 / 1] | BOOL | Read | Coil | 1313 | 0 / 1
1706 | Al_Offline_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Offline [0 / 1] | BOOL | Read | Coil | 1314 | 0 / 1
1707 | Al_Offline_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Offline [0 / 1] | BOOL | Read | Coil | 1315 | 0 / 1
1708 | Al_Offline_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Offline [0 / 1] | BOOL | Read | Coil | 1316 | 0 / 1
1709 | Al_Offline_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Offline [0 / 1] | BOOL | Read | Coil | 1317 | 0 / 1
1710 | Al_Offline_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Offline [0 / 1] | BOOL | Read | Coil | 1318 | 0 / 1
1711 | Al_Offline_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Offline [0 / 1] | BOOL | Read | Coil | 1319 | 0 / 1
1712 | Al_Offline_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Offline [0 / 1] | BOOL | Read | Coil | 1320 | 0 / 1
1713 | Al_Offline_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Offline [0 / 1] | BOOL | Read | Coil | 1321 | 0 / 1
1714 | Al_Offline_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Offline [0 / 1] | BOOL | Read | Coil | 1322 | 0 / 1
1715 | Al_Offline_THTN_1.Active | AL - Alarm - HMI Basic - Offline [0 / 1] | BOOL | Read | Coil | 1323 | 0 / 1
1716 | Al_Option_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Option [0 / 1] | BOOL | Read | Coil | 1324 | 0 / 1
1717 | Al_Option_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Option [0 / 1] | BOOL | Read | Coil | 1325 | 0 / 1
1718 | Al_Option_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Option [0 / 1] | BOOL | Read | Coil | 1326 | 0 / 1
1719 | Al_Option_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Option [0 / 1] | BOOL | Read | Coil | 1327 | 0 / 1
1720 | Al_Option_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Option [0 / 1] | BOOL | Read | Coil | 1328 | 0 / 1
1721 | Al_Option_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Option [0 / 1] | BOOL | Read | Coil | 1329 | 0 / 1
1722 | Al_Option_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Option [0 / 1] | BOOL | Read | Coil | 1330 | 0 / 1
1723 | Al_Option_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Option [0 / 1] | BOOL | Read | Coil | 1331 | 0 / 1
1724 | Al_Option_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Option [0 / 1] | BOOL | Read | Coil | 1332 | 0 / 1
1725 | Al_Option_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Option [0 / 1] | BOOL | Read | Coil | 1333 | 0 / 1
1726 | Al_Option_Rotary.Active | AL - Alarm - Rotary - Option [0 / 1] | BOOL | Read | Coil | 1334 | 0 / 1
1727 | Al_Option_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Option [0 / 1] | BOOL | Read | Coil | 1335 | 0 / 1
1728 | Al_Option_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Option [0 / 1] | BOOL | Read | Coil | 1336 | 0 / 1
1729 | Al_Option_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Option [0 / 1] | BOOL | Read | Coil | 1337 | 0 / 1
1730 | Al_Option_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Option [0 / 1] | BOOL | Read | Coil | 1338 | 0 / 1
1731 | Al_Option_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Option [0 / 1] | BOOL | Read | Coil | 1339 | 0 / 1
1732 | Al_Option_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Option [0 / 1] | BOOL | Read | Coil | 1340 | 0 / 1
1733 | Al_Option_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Option [0 / 1] | BOOL | Read | Coil | 1341 | 0 / 1
1734 | Al_Option_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Option [0 / 1] | BOOL | Read | Coil | 1342 | 0 / 1
1735 | Al_Option_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Option [0 / 1] | BOOL | Read | Coil | 1343 | 0 / 1
1736 | Al_Option_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Option [0 / 1] | BOOL | Read | Coil | 1344 | 0 / 1
1737 | Al_Overcurrent_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Over Current [0 / 1] | BOOL | Read | Coil | 1345 | 0 / 1
1738 | Al_Overcurrent_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Over Current [0 / 1] | BOOL | Read | Coil | 1346 | 0 / 1
1739 | Al_Overcurrent_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Over Current [0 / 1] | BOOL | Read | Coil | 1347 | 0 / 1
1740 | Al_Overcurrent_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Over Current [0 / 1] | BOOL | Read | Coil | 1348 | 0 / 1
1741 | Al_Overcurrent_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Over Current [0 / 1] | BOOL | Read | Coil | 1349 | 0 / 1
1742 | Al_Overcurrent_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Over current [0 / 1] | BOOL | Read | Coil | 1350 | 0 / 1
1743 | Al_Overcurrent_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Over Current [0 / 1] | BOOL | Read | Coil | 1351 | 0 / 1
1744 | Al_Overcurrent_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Over Current [0 / 1] | BOOL | Read | Coil | 1352 | 0 / 1
1745 | Al_Overcurrent_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Over Current [0 / 1] | BOOL | Read | Coil | 1353 | 0 / 1
1746 | Al_Overcurrent_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Over Current [0 / 1] | BOOL | Read | Coil | 1354 | 0 / 1
1747 | Al_Overcurrent_Rotary.Active | AL - Alarm - Rotary - OverCurrent [0 / 1] | BOOL | Read | Coil | 1355 | 0 / 1
1748 | Al_Overcurrent_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Over current [0 / 1] | BOOL | Read | Coil | 1356 | 0 / 1
1749 | Al_Overcurrent_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Over Current [0 / 1] | BOOL | Read | Coil | 1357 | 0 / 1
1750 | Al_Overcurrent_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Over Current [0 / 1] | BOOL | Read | Coil | 1358 | 0 / 1
1751 | Al_Overcurrent_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Over Current [0 / 1] | BOOL | Read | Coil | 1359 | 0 / 1
1752 | Al_Overcurrent_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Over Current [0 / 1] | BOOL | Read | Coil | 1360 | 0 / 1
1753 | Al_Overcurrent_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Over current [0 / 1] | BOOL | Read | Coil | 1361 | 0 / 1
1754 | Al_Overcurrent_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Over Current [0 / 1] | BOOL | Read | Coil | 1362 | 0 / 1
1755 | Al_Overcurrent_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Over Current [0 / 1] | BOOL | Read | Coil | 1363 | 0 / 1
1756 | Al_Overcurrent_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Over Current [0 / 1] | BOOL | Read | Coil | 1364 | 0 / 1
1757 | Al_Overcurrent_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Over Current [0 / 1] | BOOL | Read | Coil | 1365 | 0 / 1
1758 | Al_OverVolt_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1366 | 0 / 1
1759 | Al_OverVolt_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1367 | 0 / 1
1760 | Al_OverVolt_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1368 | 0 / 1
1761 | Al_OverVolt_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1369 | 0 / 1
1762 | Al_OverVolt_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1370 | 0 / 1
1763 | Al_OverVolt_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Over voltage [0 / 1] | BOOL | Read | Coil | 1371 | 0 / 1
1764 | Al_OverVolt_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1372 | 0 / 1
1765 | Al_OverVolt_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1373 | 0 / 1
1766 | Al_OverVolt_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1374 | 0 / 1
1767 | Al_OverVolt_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1375 | 0 / 1
1768 | Al_OverVolt_Rotary.Active | AL - Alarm - Rotary - OverVoltage [0 / 1] | BOOL | Read | Coil | 1376 | 0 / 1
1769 | Al_OverVolt_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Over voltage [0 / 1] | BOOL | Read | Coil | 1377 | 0 / 1
1770 | Al_OverVolt_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1378 | 0 / 1
1771 | Al_OverVolt_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1379 | 0 / 1
1772 | Al_OverVolt_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1380 | 0 / 1
1773 | Al_OverVolt_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1381 | 0 / 1
1774 | Al_OverVolt_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Over voltage [0 / 1] | BOOL | Read | Coil | 1382 | 0 / 1
1775 | Al_OverVolt_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1383 | 0 / 1
1776 | Al_OverVolt_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1384 | 0 / 1
1777 | Al_OverVolt_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1385 | 0 / 1
1778 | Al_OverVolt_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Over Voltage [0 / 1] | BOOL | Read | Coil | 1386 | 0 / 1
1779 | AL_Overvoltage_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1387 | 0 / 1
1780 | AL_Overvoltage_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1388 | 0 / 1
1781 | AL_Overvoltage_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1389 | 0 / 1
1782 | AL_Overvoltage_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1390 | 0 / 1
1783 | AL_Overvoltage_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1391 | 0 / 1
1784 | AL_Overvoltage_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1392 | 0 / 1
1785 | AL_Overvoltage_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1393 | 0 / 1
1786 | AL_Overvoltage_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1394 | 0 / 1
1787 | AL_Overvoltage_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1395 | 0 / 1
1788 | AL_Overvoltage_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1396 | 0 / 1
1789 | AL_Overvoltage_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1397 | 0 / 1
1790 | AL_Overvoltage_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1398 | 0 / 1
1791 | AL_Overvoltage_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1399 | 0 / 1
1792 | AL_Overvoltage_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1400 | 0 / 1
1793 | AL_Overvoltage_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1401 | 0 / 1
1794 | AL_Overvoltage_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1402 | 0 / 1
1795 | AL_Overvoltage_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1403 | 0 / 1
1796 | AL_Overvoltage_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1404 | 0 / 1
1797 | AL_Overvoltage_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1405 | 0 / 1
1798 | AL_Overvoltage_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Over voltage [0 / 1] | BOOL | Read | Coil | 1406 | 0 / 1
1799 | Al_Ovld_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Over Load [0 / 1] | BOOL | Read | Coil | 1407 | 0 / 1
1800 | Al_Ovld_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Over Load [0 / 1] | BOOL | Read | Coil | 1408 | 0 / 1
1801 | Al_Ovld_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Over Load [0 / 1] | BOOL | Read | Coil | 1409 | 0 / 1
1802 | Al_Ovld_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Over Load [0 / 1] | BOOL | Read | Coil | 1410 | 0 / 1
1803 | Al_Ovld_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Over Load [0 / 1] | BOOL | Read | Coil | 1411 | 0 / 1
1804 | Al_Ovld_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Over load [0 / 1] | BOOL | Read | Coil | 1412 | 0 / 1
1805 | Al_Ovld_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Over Load [0 / 1] | BOOL | Read | Coil | 1413 | 0 / 1
1806 | Al_Ovld_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Over Load [0 / 1] | BOOL | Read | Coil | 1414 | 0 / 1
1807 | Al_Ovld_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Over Load [0 / 1] | BOOL | Read | Coil | 1415 | 0 / 1
1808 | Al_Ovld_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Over Load [0 / 1] | BOOL | Read | Coil | 1416 | 0 / 1
1809 | Al_Ovld_Rotary.Active | AL - Alarm - Rotary - OverLoad [0 / 1] | BOOL | Read | Coil | 1417 | 0 / 1
1810 | Al_Ovld_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Over load [0 / 1] | BOOL | Read | Coil | 1418 | 0 / 1
1811 | Al_Ovld_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Over Load [0 / 1] | BOOL | Read | Coil | 1419 | 0 / 1
1812 | Al_Ovld_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Over Load [0 / 1] | BOOL | Read | Coil | 1420 | 0 / 1
1813 | Al_Ovld_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Over Load [0 / 1] | BOOL | Read | Coil | 1421 | 0 / 1
1814 | Al_Ovld_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Over Load [0 / 1] | BOOL | Read | Coil | 1422 | 0 / 1
1815 | Al_Ovld_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Over load [0 / 1] | BOOL | Read | Coil | 1423 | 0 / 1
1816 | Al_Ovld_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Over Load [0 / 1] | BOOL | Read | Coil | 1424 | 0 / 1
1817 | Al_Ovld_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Over Load [0 / 1] | BOOL | Read | Coil | 1425 | 0 / 1
1818 | Al_Ovld_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Over Load [0 / 1] | BOOL | Read | Coil | 1426 | 0 / 1
1819 | Al_Ovld_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Over Load [0 / 1] | BOOL | Read | Coil | 1427 | 0 / 1
1820 | Al_ParamErr_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1428 | 0 / 1
1821 | Al_ParamErr_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1429 | 0 / 1
1822 | Al_ParamErr_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1430 | 0 / 1
1823 | Al_ParamErr_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1431 | 0 / 1
1824 | Al_ParamErr_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1432 | 0 / 1
1825 | Al_ParamErr_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 1433 | 0 / 1
1826 | Al_ParamErr_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1434 | 0 / 1
1827 | Al_ParamErr_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1435 | 0 / 1
1828 | Al_ParamErr_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1436 | 0 / 1
1829 | Al_ParamErr_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1437 | 0 / 1
1830 | Al_ParamErr_Rotary.Active | AL - Alarm - Rotary - Parameters Error [0 / 1] | BOOL | Read | Coil | 1438 | 0 / 1
1831 | Al_ParamErr_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 1439 | 0 / 1
1832 | Al_ParamErr_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1440 | 0 / 1
1833 | Al_ParamErr_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1441 | 0 / 1
1834 | Al_ParamErr_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1442 | 0 / 1
1835 | Al_ParamErr_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1443 | 0 / 1
1836 | Al_ParamErr_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Parameter save Error [0 / 1] | BOOL | Read | Coil | 1444 | 0 / 1
1837 | Al_ParamErr_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1445 | 0 / 1
1838 | Al_ParamErr_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1446 | 0 / 1
1839 | Al_ParamErr_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1447 | 0 / 1
1840 | Al_ParamErr_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Parameters Error [0 / 1] | BOOL | Read | Coil | 1448 | 0 / 1
1841 | AL_ParametersCRC_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1449 | 0 / 1
1842 | AL_ParametersCRC_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1450 | 0 / 1
1843 | AL_ParametersCRC_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1451 | 0 / 1
1844 | AL_ParametersCRC_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1452 | 0 / 1
1845 | AL_ParametersCRC_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1453 | 0 / 1
1846 | AL_ParametersCRC_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1454 | 0 / 1
1847 | AL_ParametersCRC_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1455 | 0 / 1
1848 | AL_ParametersCRC_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1456 | 0 / 1
1849 | AL_ParametersCRC_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1457 | 0 / 1
1850 | AL_ParametersCRC_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1458 | 0 / 1
1851 | AL_ParametersCRC_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1459 | 0 / 1
1852 | AL_ParametersCRC_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1460 | 0 / 1
1853 | AL_ParametersCRC_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1461 | 0 / 1
1854 | AL_ParametersCRC_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1462 | 0 / 1
1855 | AL_ParametersCRC_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1463 | 0 / 1
1856 | AL_ParametersCRC_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1464 | 0 / 1
1857 | AL_ParametersCRC_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1465 | 0 / 1
1858 | AL_ParametersCRC_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1466 | 0 / 1
1859 | AL_ParametersCRC_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1467 | 0 / 1
1860 | AL_ParametersCRC_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Parameters CRC [0 / 1] | BOOL | Read | Coil | 1468 | 0 / 1
1861 | AL_PhaseLoss_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1469 | 0 / 1
1862 | AL_PhaseLoss_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1470 | 0 / 1
1863 | AL_PhaseLoss_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1471 | 0 / 1
1864 | AL_PhaseLoss_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1472 | 0 / 1
1865 | AL_PhaseLoss_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1473 | 0 / 1
1866 | AL_PhaseLoss_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1474 | 0 / 1
1867 | AL_PhaseLoss_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1475 | 0 / 1
1868 | AL_PhaseLoss_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1476 | 0 / 1
1869 | AL_PhaseLoss_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1477 | 0 / 1
1870 | AL_PhaseLoss_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1478 | 0 / 1
1871 | AL_PhaseLoss_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1479 | 0 / 1
1872 | AL_PhaseLoss_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1480 | 0 / 1
1873 | AL_PhaseLoss_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1481 | 0 / 1
1874 | AL_PhaseLoss_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1482 | 0 / 1
1875 | AL_PhaseLoss_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1483 | 0 / 1
1876 | AL_PhaseLoss_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1484 | 0 / 1
1877 | AL_PhaseLoss_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1485 | 0 / 1
1878 | AL_PhaseLoss_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1486 | 0 / 1
1879 | AL_PhaseLoss_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1487 | 0 / 1
1880 | AL_PhaseLoss_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Phase Loss [0 / 1] | BOOL | Read | Coil | 1488 | 0 / 1
1881 | Al_PhLost_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1489 | 0 / 1
1882 | Al_PhLost_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1490 | 0 / 1
1883 | Al_PhLost_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1491 | 0 / 1
1884 | Al_PhLost_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1492 | 0 / 1
1885 | Al_PhLost_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1493 | 0 / 1
1886 | Al_PhLost_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1494 | 0 / 1
1887 | Al_PhLost_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1495 | 0 / 1
1888 | Al_PhLost_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1496 | 0 / 1
1889 | Al_PhLost_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1497 | 0 / 1
1890 | Al_PhLost_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1498 | 0 / 1
1891 | Al_PhLost_Rotary.Active | AL - Alarm - Rotary - Phase Lost [0 / 1] | BOOL | Read | Coil | 1499 | 0 / 1
1892 | Al_PhLost_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1500 | 0 / 1
1893 | Al_PhLost_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1501 | 0 / 1
1894 | Al_PhLost_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1502 | 0 / 1
1895 | Al_PhLost_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1503 | 0 / 1
1896 | Al_PhLost_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1504 | 0 / 1
1897 | Al_PhLost_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1505 | 0 / 1
1898 | Al_PhLost_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1506 | 0 / 1
1899 | Al_PhLost_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1507 | 0 / 1
1900 | Al_PhLost_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1508 | 0 / 1
1901 | Al_PhLost_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Phase Lost [0 / 1] | BOOL | Read | Coil | 1509 | 0 / 1
1902 | Al_PhOpen_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Phase Open [0 / 1] | BOOL | Read | Coil | 1510 | 0 / 1
1903 | Al_PhOpen_ExhFan_10.Active | AL - Alarm - Fan Return 10 - Phase Open [0 / 1] | BOOL | Read | Coil | 1511 | 0 / 1
1904 | Al_PhOpen_ExhFan_2.Active | AL - Alarm - Fan Return 2 - Phase Open [0 / 1] | BOOL | Read | Coil | 1512 | 0 / 1
1905 | Al_PhOpen_ExhFan_3.Active | AL - Alarm - Fan Return 3 - Phase Open [0 / 1] | BOOL | Read | Coil | 1513 | 0 / 1
1906 | Al_PhOpen_ExhFan_4.Active | AL - Alarm - Fan Return 4 - Phase Open [0 / 1] | BOOL | Read | Coil | 1514 | 0 / 1
1907 | Al_PhOpen_ExhFan_5.Active | AL - Alarm - Fan Return 5 - Phase Open [0 / 1] | BOOL | Read | Coil | 1515 | 0 / 1
1908 | Al_PhOpen_ExhFan_6.Active | AL - Alarm - Fan Return 6 - Phase Open [0 / 1] | BOOL | Read | Coil | 1516 | 0 / 1
1909 | Al_PhOpen_ExhFan_7.Active | AL - Alarm - Fan Return 7 - Phase Open [0 / 1] | BOOL | Read | Coil | 1517 | 0 / 1
1910 | Al_PhOpen_ExhFan_8.Active | AL - Alarm - Fan Return 8 - Phase Open [0 / 1] | BOOL | Read | Coil | 1518 | 0 / 1
1911 | Al_PhOpen_ExhFan_9.Active | AL - Alarm - Fan Return 9 - Phase Open [0 / 1] | BOOL | Read | Coil | 1519 | 0 / 1
1912 | Al_PhOpen_Rotary.Active | AL - Alarm - Rotary - Phase Open [0 / 1] | BOOL | Read | Coil | 1520 | 0 / 1
1913 | Al_PhOpen_SupFan_1.Active | AL - Alarm - Fan Supply 1 - Phase Open [0 / 1] | BOOL | Read | Coil | 1521 | 0 / 1
1914 | Al_PhOpen_SupFan_10.Active | AL - Alarm - Fan Supply 10 - Phase Open [0 / 1] | BOOL | Read | Coil | 1522 | 0 / 1
1915 | Al_PhOpen_SupFan_2.Active | AL - Alarm - Fan Supply 2 - Phase Open [0 / 1] | BOOL | Read | Coil | 1523 | 0 / 1
1916 | Al_PhOpen_SupFan_3.Active | AL - Alarm - Fan Supply 3 - Phase Open [0 / 1] | BOOL | Read | Coil | 1524 | 0 / 1
1917 | Al_PhOpen_SupFan_4.Active | AL - Alarm - Fan Supply 4 - Phase Open [0 / 1] | BOOL | Read | Coil | 1525 | 0 / 1
1918 | Al_PhOpen_SupFan_5.Active | AL - Alarm - Fan Supply 5 - Phase Open [0 / 1] | BOOL | Read | Coil | 1526 | 0 / 1
1919 | Al_PhOpen_SupFan_6.Active | AL - Alarm - Fan Supply 6 - Phase Open [0 / 1] | BOOL | Read | Coil | 1527 | 0 / 1
1920 | Al_PhOpen_SupFan_7.Active | AL - Alarm - Fan Supply 7 - Phase Open [0 / 1] | BOOL | Read | Coil | 1528 | 0 / 1
1921 | Al_PhOpen_SupFan_8.Active | AL - Alarm - Fan Supply 8 - Phase Open [0 / 1] | BOOL | Read | Coil | 1529 | 0 / 1
1922 | Al_PhOpen_SupFan_9.Active | AL - Alarm - Fan Supply 9 - Phase Open [0 / 1] | BOOL | Read | Coil | 1530 | 0 / 1
1923 | Al_PreHeatCoilTempPrb.Active | AL - Alarm - Probe - Temperature Water PreHeating Coil [0 / 1] | BOOL | Read | Coil | 1531 | 0 / 1
1924 | Al_RDT_Fan.Active | AL - Alarm - Fan Group [0 / 1] | BOOL | Read | Coil | 1532 | 0 / 1
1925 | Al_RecSupplyTemp.Active | AL - Alarm - Probe - Supply Recovery Temperature [0 / 1] | BOOL | Read | Coil | 1533 | 0 / 1
1926 | Al_ReheatCoilWorkHrsWarn.Active | AL - Alarm - ReHeatCoil - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 1534 | 0 / 1
1927 | Al_retain.Active | AL - Alarm - Retain [0 / 1] | BOOL | Read | Coil | 1535 | 0 / 1
1928 | Al_RetAir_CO2_Lev_Prb.Active | AL - Alarm - Probe - CO2 Return Level Probe [0 / 1] | BOOL | Read | Coil | 1536 | 0 / 1
1929 | Al_RetAirFlwSwWarn.Active | AL - Alarm - Probe - Air Flow Return SW Warning [0 / 1] | BOOL | Read | Coil | 1537 | 0 / 1
1930 | Al_RetAirP_Prb.Active | AL - Alarm - Probe - Pressure Return Air [0 / 1] | BOOL | Read | Coil | 1538 | 0 / 1
1931 | Al_RetFanWorkHrsWarn.Active | AL - Alarm - Fan Return - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 1539 | 0 / 1
1932 | Al_RetFilt.Active | AL - Alarm - Filter - Return [0 / 1] | BOOL | Read | Coil | 1540 | 0 / 1
1933 | Al_RetTempPrb.Active | AL - Alarm - Probe - Return Temperature [0 / 1] | BOOL | Read | Coil | 1541 | 0 / 1
1934 | Al_SupplyAirFlwSwWarn.Active | AL - Alarm - Probe - Supply Air Flow SW Warning [0 / 1] | BOOL | Read | Coil | 1542 | 0 / 1
1935 | Al_SupplyAirP_Prb.Active | AL - Alarm - Probe - Supply Air Pressure [0 / 1] | BOOL | Read | Coil | 1543 | 0 / 1
1936 | Al_SupplyFanWorkHrsWarn.Active | AL - Alarm - Fan Supply - Works Hour Warning [0 / 1] | BOOL | Read | Coil | 1544 | 0 / 1
1937 | Al_SupplyFilt.Active | AL - Alarm - Filter - Supply [0 / 1] | BOOL | Read | Coil | 1545 | 0 / 1
1938 | Al_SupplyTempPrb.Active | AL - Alarm - Probe - Supply Temperature [0 / 1] | BOOL | Read | Coil | 1546 | 0 / 1
1939 | Al_SwPrototype.Active | AL - Alarm - Software Version - Prototype [0 / 1] | BOOL | Read | Coil | 1547 | 0 / 1
1940 | Al_ThTune_ClkBrd.Active | AL - Alarm - HMI Basic - Clock Board [0 / 1] | BOOL | Read | Coil | 1548 | 0 / 1
1941 | Al_ThTune_HumPrb.Active | AL - Alarm - HMI Basic - Humidity Probe [0 / 1] | BOOL | Read | Coil | 1549 | 0 / 1
1942 | Al_ThTune_TempPrb.Active | AL - Alarm - HMI Basic - Temperature Probe [0 / 1] | BOOL | Read | Coil | 1550 | 0 / 1
1943 | Al_TooHot_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1551 | 0 / 1
1944 | Al_TooHot_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1552 | 0 / 1
1945 | Al_TooHot_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1553 | 0 / 1
1946 | Al_TooHot_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1554 | 0 / 1
1947 | Al_TooHot_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1555 | 0 / 1
1948 | Al_TooHot_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1556 | 0 / 1
1949 | Al_TooHot_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1557 | 0 / 1
1950 | Al_TooHot_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1558 | 0 / 1
1951 | Al_TooHot_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1559 | 0 / 1
1952 | Al_TooHot_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1560 | 0 / 1
1953 | Al_TooHot_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1561 | 0 / 1
1954 | Al_TooHot_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1562 | 0 / 1
1955 | Al_TooHot_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1563 | 0 / 1
1956 | Al_TooHot_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1564 | 0 / 1
1957 | Al_TooHot_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1565 | 0 / 1
1958 | Al_TooHot_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1566 | 0 / 1
1959 | Al_TooHot_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1567 | 0 / 1
1960 | Al_TooHot_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1568 | 0 / 1
1961 | Al_TooHot_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1569 | 0 / 1
1962 | Al_TooHot_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - TooHot [0 / 1] | BOOL | Read | Coil | 1570 | 0 / 1
1963 | Al_Undervoltage_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1571 | 0 / 1
1964 | Al_Undervoltage_EC_ExhFan10.Active | AL - Alarm - Fan Return 10 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1572 | 0 / 1
1965 | Al_Undervoltage_EC_ExhFan2.Active | AL - Alarm - Fan Return 2 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1573 | 0 / 1
1966 | Al_Undervoltage_EC_ExhFan3.Active | AL - Alarm - Fan Return 3 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1574 | 0 / 1
1967 | Al_Undervoltage_EC_ExhFan4.Active | AL - Alarm - Fan Return 4 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1575 | 0 / 1
1968 | Al_Undervoltage_EC_ExhFan5.Active | AL - Alarm - Fan Return 5 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1576 | 0 / 1
1969 | Al_Undervoltage_EC_ExhFan6.Active | AL - Alarm - Fan Return 6 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1577 | 0 / 1
1970 | Al_Undervoltage_EC_ExhFan7.Active | AL - Alarm - Fan Return 7 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1578 | 0 / 1
1971 | Al_Undervoltage_EC_ExhFan8.Active | AL - Alarm - Fan Return 8 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1579 | 0 / 1
1972 | Al_Undervoltage_EC_ExhFan9.Active | AL - Alarm - Fan Return 9 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1580 | 0 / 1
1973 | Al_Undervoltage_EC_SupFan1.Active | AL - Alarm - Fan Supply 1 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1581 | 0 / 1
1974 | Al_Undervoltage_EC_SupFan10.Active | AL - Alarm - Fan Supply 10 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1582 | 0 / 1
1975 | Al_Undervoltage_EC_SupFan2.Active | AL - Alarm - Fan Supply 2 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1583 | 0 / 1
1976 | Al_Undervoltage_EC_SupFan3.Active | AL - Alarm - Fan Supply 3 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1584 | 0 / 1
1977 | Al_Undervoltage_EC_SupFan4.Active | AL - Alarm - Fan Supply 4 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1585 | 0 / 1
1978 | Al_Undervoltage_EC_SupFan5.Active | AL - Alarm - Fan Supply 5 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1586 | 0 / 1
1979 | Al_Undervoltage_EC_SupFan6.Active | AL - Alarm - Fan Supply 6 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1587 | 0 / 1
1980 | Al_Undervoltage_EC_SupFan7.Active | AL - Alarm - Fan Supply 7 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1588 | 0 / 1
1981 | Al_Undervoltage_EC_SupFan8.Active | AL - Alarm - Fan Supply 8 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1589 | 0 / 1
1982 | Al_Undervoltage_EC_SupFan9.Active | AL - Alarm - Fan Supply 9 EC - Undervoltage [0 / 1] | BOOL | Read | Coil | 1590 | 0 / 1
1983 | CfgErrAlrm.Active | AL - Alarm - Device - Wrong configuration [0 / 1] | BOOL | Read | Coil | 1591 | 0 / 1
1984 | Al_MotorFault_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Motor Fault [0 / 1] | BOOL | Read | Coil | 1592 | 0 / 1
1985 | OfflineAlrm.Active | AL - Alarm - Device - Offline [0 / 1] | BOOL | Read | Coil | 1593 | 0 / 1
1986 | Al_Offline_IO_PCB.Active | AL - Alarm - Module IO - EC-PCB - Offline [0 / 1] | BOOL | Read | Coil | 1594 | 0 / 1
1987 | Al_DXRev.Active | AL - Alarm - Reverse unit [0 / 1] | BOOL | Read | Coil | 1595 | 0 / 1
1988 | Al_WarningFilterHigh.Active | AL - Alarm - Filter - High pressure [0 / 1] | BOOL | Read | Coil | 1596 | 0 / 1
1989 | Al_RRG_WorkConfirm.Active | AL - Alarm - Recovery - Rotary - Work confirm [0 / 1] | BOOL | Read | Coil | 1597 | 0 / 1
1990 | Al_ClkBrd_THTN_1.Active | AL - Alarm - HMI Basic - Clock Board [0 / 1] | BOOL | Read | Coil | 1598 | 0 / 1
1991 | Al_ClkBrd_THTN_1.Trigger | AL - Alarm - HMI Basic - Clock Board [0 / 1] | BOOL | Read | Coil | 1599 | 0 / 1
1992 | Al_DXRev.Trigger | AL - Alarm - Reverse unit [0 / 1] | BOOL | Read | Coil | 1600 | 0 / 1
1993 | Al_HumPrb_THTN_1.Active | AL - Alarm - HMI Basic - Humidity sensor [0 / 1] | BOOL | Read | Coil | 1601 | 0 / 1
1994 | Al_HumPrb_THTN_1.Trigger | AL - Alarm - HMI Basic - Humidity sensor [0 / 1] | BOOL | Read | Coil | 1602 | 0 / 1
1995 | Al_Offline_IO_PCB.Trigger | AL - Alarm - Module IO - EC-PCB - Offline [0 / 1] | BOOL | Read | Coil | 1603 | 0 / 1
1996 | Al_RRG_WorkConfirm.Trigger | AL - Alarm - Recovery - Rotary - Work confirm [0 / 1] | BOOL | Read | Coil | 1604 | 0 / 1
1997 | Al_TempPrb_THTN_1.Active | AL - Alarm - HMI Basic - Temperature sensor [0 / 1] | BOOL | Read | Coil | 1605 | 0 / 1
1998 | Al_TempPrb_THTN_1.Trigger | AL - Alarm - HMI Basic - Temperature sensor [0 / 1] | BOOL | Read | Coil | 1606 | 0 / 1
1999 | Al_WarningFilterHigh.Trigger | AL - Alarm - Filter - Pressure High [0 / 1] | BOOL | Read | Coil | 1607 | 0 / 1
2000 | CfgErrAlrm_CPCOE_1.Active | AL - Alarm - Module IO - cPCOE - Configuration [0 / 1] | BOOL | Read | Coil | 1608 | 0 / 1
2001 | CfgErrAlrm_CPCOE_1.Trigger | AL - Alarm - Module IO - cPCOE - Configuration [0 / 1] | BOOL | Read | Coil | 1609 | 0 / 1
2002 | OfflineAlrm_CPCOE_1.Active | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | BOOL | Read | Coil | 1610 | 0 / 1
2003 | OfflineAlrm_CPCOE_1.Trigger | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | BOOL | Read | Coil | 1611 | 0 / 1
2005 | EnDate | CLK - Time - Setting - Change Enable [0 / 1] | BOOL | ReadWrite | Coil | 1612 | 0 / 1 | 0 - NO 1 - YES
2029 | Cool_1.Logic | PAR - Cooling - Main Cooler - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1613 | 0 / 1 | 0 - NC 1 - NO
2031 | Cool_2.Logic | PAR - Cooling - Main Cooler DX - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1614 | 0 / 1 | 0 - NC 1 - NO
2066 | En_CoolRec | PAR - Recovery - Cooling - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1615 | 0 / 1 | 0 - NO 1 - YES
2067 | En_FreeCoolHeat | PAR - System - Free Cool/Heat - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1616 | 0 / 1 | 0 - NO 1 - YES
2068 | En_Rev_MixDamper | PAR - Mixing damper - Reverse signal [0 / 1] | BOOL | ReadWrite | Coil | 1617 | 0 / 1 | 0 - NO 1 - YES
2069 | En_Rev_Recovery | PAR - Recovery - Reverse signal [0 / 1] | BOOL | ReadWrite | Coil | 1618 | 0 / 1 | 0 - NO 1 - YES
2073 | FastHeatEn | PAR - Recovery - Fast Heating - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1619 | 0 / 1 | 0 - NO 1 - YES
2074 | FastHeatStop | PAR - Recovery - Stop Fast Heat - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1620 | 0 / 1 | 0 - NO 1 - YES
2077 | FastHeatTrig | PAR - Recovery - Start Fast Heat - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1621 | 0 / 1 | 0 - NO 1 - YES
2086 | HC_Cool_1.Res | PAR - Cooling - Main Cooler - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1622 | 0 / 1 | 0 - NO 1 - YES
2087 | HC_Cool_2.Res | PAR - Cooling - Main Cooler DX - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1623 | 0 / 1 | 0 - NO 1 - YES
2088 | HC_ExhFan_1.Res | PAR - Fan - Return 1 - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1624 | 0 / 1 | 0 - NO 1 - YES
2089 | HC_ExhFan_2.Res | PAR - Fan - Return 2 - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1625 | 0 / 1 | 0 - NO 1 - YES
2090 | HC_Heat_1.Res | PAR - Heating - Main Heater - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1626 | 0 / 1 | 0 - NO 1 - YES
2091 | HC_Heat_2.Res | PAR - Heating - Main Device 2 - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1627 | 0 / 1 | 0 - NO 1 - YES
2092 | HC_Hum.Res | PAR - Humidity - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1628 | 0 / 1 | 0 - NO 1 - YES
2093 | HC_PreHeat.Res | PAR - Heating - PreHeating - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1629 | 0 / 1 | 0 - NO 1 - YES
2094 | HC_RecoveryPump.Res | PAR - Recovery - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1630 | 0 / 1 | 0 - NO 1 - YES
2095 | HC_ReHeat.Res | PAR - Heating - ReHeating - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1631 | 0 / 1 | 0 - NO 1 - YES
2096 | HC_SupplyFan_1.Res | PAR - Fan - Supply 1 - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1632 | 0 / 1 | 0 - NO 1 - YES
2097 | HC_SupplyFan_2.Res | PAR - Fan - Supply 2 - Reset [0 / 1] | BOOL | ReadWrite | Coil | 1633 | 0 / 1 | 0 - NO 1 - YES
2101 | Heat_1.Logic | PAR - Heating - Main Heater - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1634 | 0 / 1 | 0 - NC 1 - NO
2109 | Hum.Logic | PAR - Humidity - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1635 | 0 / 1 | 0 - NC 1 - NO
2151 | PreHeaterPump.Logic | PAR - Heating - PreHeating - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1636 | 0 / 1 | 0 - NC 1 - NO
2163 | RecoveryPump.Logic | PAR - Recovery - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1637 | 0 / 1 | 0 - NC 1 - NO
2165 | ReHeat.Logic | PAR - Heating - ReHeating - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1638 | 0 / 1 | 0 - NC 1 - NO
2178 | RevOut_1.Logic | PAR - Heating - Reverse Device 1 - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1639 | 0 / 1 | 0 - NC 1 - NO
2180 | RevOut_2.Logic | PAR - Heating - Reverse Device 2 - Logic [0 / 1] | BOOL | ReadWrite | Coil | 1640 | 0 / 1 | 0 - NC 1 - NO
2244 | LowSupplyTemp_Off | PAR - Heating - Supply Limit - Threshold unit STOP [0 / 1] | BOOL | ReadWrite | Coil | 1641 | 0 / 1 | 0 - NO 1 - YES
2245 | PreHeat_Always | PAR - Heating - Main Heater HW - Pre-Heat always start [0 / 1] | BOOL | ReadWrite | Coil | 1642 | 0 / 1 | 0 - NO 1 - YES
2253 | DoubleFanRot_Manual | PAR - Fan - Redundant - Manual rotation [0 / 1] | BOOL | ReadWrite | Coil | 1643 | 0 / 1 | 0 - NO 1 - YES
2255 | FanTempReg | PAR - Fan - Temperature regulation - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1644 | 0 / 1 | 0 - NO 1 - YES
2260 | RRG_0_10V | PAR - Recovery - Rotery - Enable 0-10V on Y3 for RRG [0 / 1] | BOOL | ReadWrite | Coil | 1645 | 0 / 1 | 0 - NO 1 - YES
2261 | En_RRG_Alarm | PAR - Recovery - Rotery - Alarm enable [0 / 1] | BOOL | ReadWrite | Coil | 1646 | 0 / 1 | 0 - NO 1 - YES
2265 | Mix_Mode_ECO | PAR - Mixing - Manual mode ECO - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1647 | 0 / 1 | 0 - NO 1 - YES
2267 | Mix_Mode_OPTIMAL | PAR - Mixing - Manual mode Optimal - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1648 | 0 / 1 | 0 - NO 1 - YES
2269 | Mix_Mode_COMFORT | PAR - Mixing - Manual mode Comfort - Enable [0 / 1] | BOOL | ReadWrite | Coil | 1649 | 0 / 1 | 0 - NO 1 - YES
2282 | AfterPreHeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - After PreHeat [0 / 1] | BOOL | ReadWrite | Coil | 1650 | 0 / 1 | 0 - NO 1 - YES
2294 | AppCool_CW | SYS - Application Code - Cooling coil [0 / 1] | BOOL | ReadWrite | Coil | 1651 | 0 / 1 | 0 - NO 1 - YES
2295 | AppCool_DX | SYS - Application Code - Direct Expansion [0 / 1] | BOOL | ReadWrite | Coil | 1652 | 0 / 1 | 0 - NO 1 - YES
2296 | AppEco | SYS - Application Code - Mixing damper [0 / 1] | BOOL | ReadWrite | Coil | 1653 | 0 / 1 | 0 - NO 1 - YES
2297 | AppHeat_DX | SYS - Application Code - Heat - Direct Expansion [0 / 1] | BOOL | ReadWrite | Coil | 1654 | 0 / 1 | 0 - NO 1 - YES
2298 | AppHeat_HE | SYS - Application Code - Electric Heating [0 / 1] | BOOL | ReadWrite | Coil | 1655 | 0 / 1 | 0 - NO 1 - YES
2299 | AppHeat_HW | SYS - Application Code - Heating Coil [0 / 1] | BOOL | ReadWrite | Coil | 1656 | 0 / 1 | 0 - NO 1 - YES
2300 | AppHeat_Steam | SYS - Application Code - Heating Steam [0 / 1] | BOOL | ReadWrite | Coil | 1657 | 0 / 1 | 0 - NO 1 - YES
2301 | AppHum_Evap | SYS - Application Code - Humidity - Evap [0 / 1] | BOOL | ReadWrite | Coil | 1658 | 0 / 1 | 0 - NO 1 - YES
2302 | AppHum_Steam | SYS - Application Code - Humidity - Steam [0 / 1] | BOOL | ReadWrite | Coil | 1659 | 0 / 1 | 0 - NO 1 - YES
2304 | AppPreHeat_DX | SYS - Application Code - PreHeat_DX [0 / 1] | BOOL | ReadWrite | Coil | 1660 | 0 / 1 | 0 - NO 1 - YES
2305 | AppPreHeat_HE | SYS - Application Code - PreHeat_HE [0 / 1] | BOOL | ReadWrite | Coil | 1661 | 0 / 1 | 0 - NO 1 - YES
2306 | AppPreHeat_HW | SYS - Application Code - PreHeat_HW [0 / 1] | BOOL | ReadWrite | Coil | 1662 | 0 / 1 | 0 - NO 1 - YES
2307 | AppRec_EnExh | SYS - Application Code - Return [0 / 1] | BOOL | ReadWrite | Coil | 1663 | 0 / 1 | 0 - NO 1 - YES
2308 | AppRec_Glycol | SYS - Application Code - Rec_Glycol [0 / 1] | BOOL | ReadWrite | Coil | 1664 | 0 / 1 | 0 - NO 1 - YES
2309 | AppRec_Plate | SYS - Application Code - Rec_Plate [0 / 1] | BOOL | ReadWrite | Coil | 1665 | 0 / 1 | 0 - NO 1 - YES
2310 | AppRec_Rotary | SYS - Application Code - Recovery - Rotary [0 / 1] | BOOL | ReadWrite | Coil | 1666 | 0 / 1 | 0 - NO 1 - YES
2311 | AppRec_SupplyOnly | SYS - Application Code - Rec_SupplyOnly [0 / 1] | BOOL | ReadWrite | Coil | 1667 | 0 / 1 | 0 - NO 1 - YES
2312 | AppReg_Ret | SYS - Application Code - Reg_Ret [0 / 1] | BOOL | ReadWrite | Coil | 1668 | 0 / 1 | 0 - NO 1 - YES
2313 | AppReg_Room | SYS - Application Code - Reg_Room [0 / 1] | BOOL | ReadWrite | Coil | 1669 | 0 / 1 | 0 - NO 1 - YES
2314 | AppReg_Supply | SYS - Application Code - Reg_Supply [0 / 1] | BOOL | ReadWrite | Coil | 1670 | 0 / 1 | 0 - NO 1 - YES
2315 | AppReHeat_DX | SYS - Application Code - ReHeat_DX [0 / 1] | BOOL | ReadWrite | Coil | 1671 | 0 / 1 | 0 - NO 1 - YES
2316 | AppReHeat_HE | SYS - Application Code - ReHeat_HE [0 / 1] | BOOL | ReadWrite | Coil | 1672 | 0 / 1 | 0 - NO 1 - YES
2317 | AppReHeat_HW | SYS - Application Code - ReHeat_HW [0 / 1] | BOOL | ReadWrite | Coil | 1673 | 0 / 1 | 0 - NO 1 - YES
2318 | AppRev_DX | SYS - Application Code - Rev_DX [0 / 1] | BOOL | ReadWrite | Coil | 1674 | 0 / 1 | 0 - NO 1 - YES
2319 | AppRev_W | SYS - Application Code - Rev_W [0 / 1] | BOOL | ReadWrite | Coil | 1675 | 0 / 1 | 0 - NO 1 - YES
2320 | AppRevCoolDX | SYS - Application Code - RevCoolDX [0 / 1] | BOOL | ReadWrite | Coil | 1676 | 0 / 1 | 0 - NO 1 - YES
2321 | AppRevCoolW | SYS - Application Code - RevCoolW [0 / 1] | BOOL | ReadWrite | Coil | 1677 | 0 / 1 | 0 - NO 1 - YES
2322 | AppRevHeatDX | SYS - Application Code - RevHeatDX [0 / 1] | BOOL | ReadWrite | Coil | 1678 | 0 / 1 | 0 - NO 1 - YES
2323 | AppRevHeatW | SYS - Application Code - RevHeatW [0 / 1] | BOOL | ReadWrite | Coil | 1679 | 0 / 1 | 0 - NO 1 - YES
2325 | BacNetSel | SYS - Unit Configuration - BacNet Port [0 / 1] | BOOL | ReadWrite | Coil | 1680 | 0 / 1 | 0 - ETHERNET 1 - PLAN
2327 | CO2_Simulation_En | SYS - IO Setting - CO2 Simulate - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 1681 | 0 / 1 | 0 - NO 1 - YES
2329 | CoolAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Cool [0 / 1] | BOOL | ReadWrite | Coil | 1682 | 0 / 1 | 0 - NC 1 - NO
2332 | En_Buzz | SYS - Unit Configuration - Enable Buzzer [0 / 1] | BOOL | ReadWrite | Coil | 1683 | 0 / 1 | 0 - NO 1 - YES
2333 | En_HumTHTN_1 | SYS - Unit Configuration - HMI Basic - Humidity Probe [0 / 1] | BOOL | ReadWrite | Coil | 1684 | 0 / 1 | 0 - NO 1 - YES
2334 | En_RetAir_CO2 | SYS - IO Setting - Enable Modbus - CO2 [0 / 1] | BOOL | ReadWrite | Coil | 1685 | 0 / 1 | 0 - NO 1 - YES
2335 | En_RetAirP | SYS - IO Setting - Enable Modbus - Pressure - Return [0 / 1] | BOOL | ReadWrite | Coil | 1686 | 0 / 1 | 0 - NO 1 - YES
2336 | En_RetHum | SYS - IO Setting - Enable Modbus - Humidity - Return [0 / 1] | BOOL | ReadWrite | Coil | 1687 | 0 / 1 | 0 - NO 1 - YES
2337 | En_SupplyAirP | SYS - IO Setting - Enable Modbus - Pressure - Supply [0 / 1] | BOOL | ReadWrite | Coil | 1688 | 0 / 1 | 0 - NO 1 - YES
2338 | En_SupplyHum | SYS - IO Setting - Enable Modbus - Humidity - Supply [0 / 1] | BOOL | ReadWrite | Coil | 1689 | 0 / 1 | 0 - NO 1 - YES
2339 | ExhAirDamp.Logic | SYS - IO Setting - Digital Output - Logic - Damper - Supply [0 / 1] | BOOL | ReadWrite | Coil | 1690 | 0 / 1 | 0 - NC 1 - NO
2344 | ExtTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - External [0 / 1] | BOOL | ReadWrite | Coil | 1691 | 0 / 1 | 0 - NO 1 - YES
2348 | FireAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm Fire [0 / 1] | BOOL | ReadWrite | Coil | 1692 | 0 / 1 | 0 - NC 1 - NO
2350 | Heat_2.Logic | SYS - IO Setting - Digital Output - Logic - Heating 2 [0 / 1] | BOOL | ReadWrite | Coil | 1693 | 0 / 1 | 0 - NC 1 - NO
2351 | HumAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Humidifier [0 / 1] | BOOL | ReadWrite | Coil | 1694 | 0 / 1 | 0 - NC 1 - NO
2353 | ID2_Alrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Heat [0 / 1] | BOOL | ReadWrite | Coil | 1695 | 0 / 1 | 0 - NC 1 - NO
2362 | RecSupplyTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Supply Recovery [0 / 1] | BOOL | ReadWrite | Coil | 1696 | 0 / 1 | 0 - NO 1 - YES
2365 | RemoteOn.Logic | SYS - IO Setting - Digital Input - Logic - Remote ON [0 / 1] | BOOL | ReadWrite | Coil | 1697 | 0 / 1 | 0 - NC 1 - NO
2367 | RetFilter.Logic | SYS - IO Setting - Digital Input - Logic - Filter - Return [0 / 1] | BOOL | ReadWrite | Coil | 1698 | 0 / 1 | 0 - NC 1 - NO
2369 | RetTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Return [0 / 1] | BOOL | ReadWrite | Coil | 1699 | 0 / 1 | 0 - NO 1 - YES
2372 | SrsAlrm.Logic | SYS - IO Setting - Digital Output - Logic - Global Alarm [0 / 1] | BOOL | ReadWrite | Coil | 1700 | 0 / 1 | 0 - NC 1 - NO
2374 | SupplyFilter.Logic | SYS - IO Setting - Digital Input - Logic - Filter - Supply [0 / 1] | BOOL | ReadWrite | Coil | 1701 | 0 / 1 | 0 - NC 1 - NO
2385 | UnitConfigured | SYS - Unit Configuration - Enabled [0 / 1] | BOOL | ReadWrite | Coil | 1702 | 0 / 1 | 0 - NO 1 - YES
2387 | W_HeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Water Heat [0 / 1] | BOOL | ReadWrite | Coil | 1703 | 0 / 1 | 0 - NO 1 - YES
2390 | W_PreHeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Water PreHeat [0 / 1] | BOOL | ReadWrite | Coil | 1704 | 0 / 1 | 0 - NO 1 - YES
2393 | WinSum.Enabled | SYS - IO Setting - Enable Inputs - Summer / Winter [0 / 1] | BOOL | ReadWrite | Coil | 1705 | 0 / 1 | 0 - NO 1 - YES
2394 | WinSum.Logic | SYS - IO Setting - Digital Input - Logic - Winter / Summer [0 / 1] | BOOL | ReadWrite | Coil | 1706 | 0 / 1 | 0 - NC 1 - NO
2397 | CurrVer.IsBeta | SYS - System - Application Version - _ . _ . _ _ _ B _ _ | BOOL | Read | Coil | 1707
2401 | ExhTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature Exhaust [0 / 1] | BOOL | Read | Coil | 1708 | 0 / 1 | 0 - NO 1 - YES
2402 | Manual_PreHeat | SYS - PreHeater - Manual mode active [0 / 1] | BOOL | Read | Coil | 1709 | 0 / 1 | 0 - NO 1 - YES
2403 | Manual_Recovery | SYS - Recovery - Manual mode active [0 / 1] | BOOL | Read | Coil | 1710 | 0 / 1 | 0 - NO 1 - YES
2404 | Manual_Heat | SYS - Heater - Manual mode active [0 / 1] | BOOL | Read | Coil | 1711 | 0 / 1 | 0 - NO 1 - YES
2405 | Manual_Cool | SYS - Cooler - Manual mode active [0 / 1] | BOOL | Read | Coil | 1712 | 0 / 1 | 0 - NO 1 - YES
2406 | Manual_ReHeat | SYS - ReHeater - Manual mode active [0 / 1] | BOOL | Read | Coil | 1713 | 0 / 1 | 0 - NO 1 - YES
2407 | Manual_Reverse | SYS - Reverse unit - Manual mode active [0 / 1] | BOOL | Read | Coil | 1714 | 0 / 1 | 0 - NO 1 - YES
2408 | Manual_Mix | SYS - Mixing damper - Manual mode active [0 / 1] | BOOL | Read | Coil | 1715 | 0 / 1 | 0 - NO 1 - YES
2409 | Manual_Humidity | SYS - Humidifier - Manual mode active [0 / 1] | BOOL | Read | Coil | 1716 | 0 / 1 | 0 - NO 1 - YES
2410 | Manual_RedDamp | SYS - Redundant Damper - Manual mode active [0 / 1] | BOOL | Read | Coil | 1717 | 0 / 1 | 0 - NO 1 - YES
2411 | Manual_Active | SYS - Manual mode active [0 / 1] | BOOL | Read | Coil | 1718 | 0 / 1 | 0 - NO 1 - YES
4651 | Manual_Active |  | Bool |  | Coil | 1718
4513 | RevOut_1_Val_DO |  | Bool |  | Coil | 1719 | 0 / 1
4512 | RevOut_2_Val_DO |  | Bool |  | Coil | 1720 | 0 / 1
4511 | Filter_Counter_Al |  | Bool |  | Coil | 1721 | 0 / 1
4510 | Res_Filter_Counter |  | Bool |  | Coil | 1722 | 0 / 1
4509 | QR_En_Compact_CBX |  | Bool |  | Coil | 1723 | 0 / 1
4508 | QR_En_Compact_RRG |  | Bool |  | Coil | 1724 | 0 / 1
4507 | QR_En_Compact_HEX |  | Bool |  | Coil | 1725 | 0 / 1
4506 | En_IO_PCB |  | Bool |  | Coil | 1726 | 0 / 1
4505 | En_MainBoard |  | Bool |  | Coil | 1727 | 0 / 1
4504 | Cool_1.HW_Val |  | Bool |  | Coil | 1728 | 0 / 1
4503 | Fire_AutoReset_En |  | Bool |  | Coil | 1729 | 0 / 1
4502 | Pres_Filtr_En |  | Bool |  | Coil | 1730 | 0 / 1
4501 | Pressure1_Simulation_En |  | Bool |  | Coil | 1731 | 0 / 1
4500 | Pressure2_Simulation_En |  | Bool |  | Coil | 1732 | 0 / 1
4499 | SupHum_Simulation_En |  | Bool |  | Coil | 1733 | 0 / 1
4498 | RetHum_Simulation_En |  | Bool |  | Coil | 1734 | 0 / 1
4497 | En_SupplyAirP_2 |  | Bool |  | Coil | 1735 | 0 / 1
4496 | En_SupplyAirP_3 |  | Bool |  | Coil | 1736 | 0 / 1
4495 | En_RetAirP_2 |  | Bool |  | Coil | 1737 | 0 / 1
4494 | PreHTempReg |  | Bool |  | Coil | 1738 | 0 / 1
4493 | DoubleDamp.Val | IO - Digital Output - Damper - Redundant [0 / 1] | Bool | Read | Coil | 1739 | 0 / 1 | 0 - ON 1 - OFF
4492 | DoubleDamp.Logic |  | Bool |  | Coil | 1740 | 0 / 1
4491 | DoubleDamp.Enabled |  | Bool |  | Coil | 1741 | 0 / 1
4490 | En_MainBoard_TempHumid |  | Bool |  | Coil | 1742 | 0 / 1
4489 | En_MainBoard_Humid |  | Bool |  | Coil | 1743 | 0 / 1
4488 | En_MainBoard_PressSup |  | Bool |  | Coil | 1744 | 0 / 1
4487 | En_MainBoard_PressRet |  | Bool |  | Coil | 1745 | 0 / 1
4486 | En_MainBoard_Filter |  | Bool |  | Coil | 1746 | 0 / 1
4485 | MB_Devices.MB_MainBoard_1.Zeroing_En |  | Bool |  | Coil | 1747 | 0 / 1
4484 | MB_Rev_Press_Fan |  | Bool |  | Coil | 1748 | 0 / 1
4483 | MB_Rev_Press_Filter |  | Bool |  | Coil | 1749 | 0 / 1
4482 | En_Fan_AI |  | Bool |  | Coil | 1750 | 0 / 1
4481 | THTune_TimeSync |  | BOOL |  | Coil | 1751 | 0 / 1
4480 | En_Basic_Res |  | Bool |  | Coil | 1752 | 0 / 1
4479 | MB_Devices.IO_PCB_1.IN1 |  | Bool |  | Coil | 1753 | 0 / 1
4478 | MB_Devices.IO_PCB_1.IN2 |  | Bool |  | Coil | 1754 | 0 / 1
4477 | En_Exh_VAV |  | Bool |  | Coil | 1755 | 0 / 1
4476 | En_Exh_CAV |  | Bool |  | Coil | 1756 | 0 / 1
4475 | En_EC_2 |  | Bool |  | Coil | 1757 | 0 / 1
4474 | En_ExhFan_2 |  | Bool |  | Coil | 1758 | 0 / 1
4473 | ExhMulti_3 |  | Bool |  | Coil | 1759 | 0 / 1
4472 | ExhMulti_4 |  | Bool |  | Coil | 1760 | 0 / 1
4471 | ExhMulti_5 |  | Bool |  | Coil | 1761 | 0 / 1
4470 | ExhMulti_6 |  | Bool |  | Coil | 1762 | 0 / 1
4469 | ExhMulti_7 |  | Bool |  | Coil | 1763 | 0 / 1
4468 | ExhMulti_8 |  | Bool |  | Coil | 1764 | 0 / 1
4467 | ExhMulti_9 |  | Bool |  | Coil | 1765 | 0 / 1
4466 | ExhMulti_10 |  | Bool |  | Coil | 1766 | 0 / 1
4465 | ExhMulti_11 |  | Bool |  | Coil | 1767 | 0 / 1
4464 | ExhMulti_12 |  | Bool |  | Coil | 1768 | 0 / 1
4463 | ExhMulti_13 |  | Bool |  | Coil | 1769 | 0 / 1
4462 | ExhMulti_14 |  | Bool |  | Coil | 1770 | 0 / 1
4461 | ExhMulti_15 |  | Bool |  | Coil | 1771 | 0 / 1
4460 | ExhMulti_2 |  | Bool |  | Coil | 1772 | 0 / 1
4459 | En_Supply_VAV |  | Bool |  | Coil | 1773 | 0 / 1
4458 | En_Supply_CAV |  | Bool |  | Coil | 1774 | 0 / 1
4457 | En_EC |  | Bool |  | Coil | 1775 | 0 / 1
4456 | En_SupplyFan_2 |  | Bool |  | Coil | 1776 | 0 / 1
4455 | SupplyMulti_2 |  | Bool |  | Coil | 1777 | 0 / 1
4454 | SupplyMulti_3 |  | Bool |  | Coil | 1778 | 0 / 1
4453 | SupplyMulti_4 |  | Bool |  | Coil | 1779 | 0 / 1
4452 | SupplyMulti_5 |  | Bool |  | Coil | 1780 | 0 / 1
4451 | SupplyMulti_6 |  | Bool |  | Coil | 1781 | 0 / 1
4450 | SupplyMulti_7 |  | Bool |  | Coil | 1782 | 0 / 1
4449 | SupplyMulti_8 |  | Bool |  | Coil | 1783 | 0 / 1
4448 | SupplyMulti_9 |  | Bool |  | Coil | 1784 | 0 / 1
4447 | SupplyMulti_10 |  | Bool |  | Coil | 1785 | 0 / 1
4446 | SupplyMulti_11 |  | Bool |  | Coil | 1786 | 0 / 1
4445 | SupplyMulti_12 |  | Bool |  | Coil | 1787 | 0 / 1
4444 | SupplyMulti_13 |  | Bool |  | Coil | 1788 | 0 / 1
4443 | SupplyMulti_14 |  | Bool |  | Coil | 1789 | 0 / 1
4442 | SupplyMulti_15 |  | Bool |  | Coil | 1790 | 0 / 1
4441 | MultiRed |  | Bool |  | Coil | 1791 | 0 / 1
4440 | SupplyMultiRed |  | Bool |  | Coil | 1792 | 0 / 1
4439 | ExhMultiRed |  | Bool |  | Coil | 1793 | 0 / 1
4438 | Al_ActiveSupFan_1 |  | BOOL |  | Coil | 1794 | 0 / 1
4437 | Al_ActiveSupFan_10 |  | BOOL |  | Coil | 1795 | 0 / 1
4436 | Al_ActiveSupFan_11 |  | BOOL |  | Coil | 1796 | 0 / 1
4435 | Al_ActiveSupFan_12 |  | BOOL |  | Coil | 1797 | 0 / 1
4434 | Al_ActiveSupFan_13 |  | BOOL |  | Coil | 1798 | 0 / 1
4433 | Al_ActiveSupFan_14 |  | BOOL |  | Coil | 1799 | 0 / 1
4432 | Al_ActiveSupFan_15 |  | BOOL |  | Coil | 1800 | 0 / 1
4431 | Al_ActiveExhFan_1 |  | BOOL |  | Coil | 1801 | 0 / 1
4430 | Al_ActiveExhFan_10 |  | BOOL |  | Coil | 1802 | 0 / 1
4429 | Al_ActiveExhFan_11 |  | BOOL |  | Coil | 1803 | 0 / 1
4428 | Al_ActiveExhFan_12 |  | BOOL |  | Coil | 1804 | 0 / 1
4427 | Al_ActiveExhFan_13 |  | BOOL |  | Coil | 1805 | 0 / 1
4426 | Al_ActiveExhFan_14 |  | BOOL |  | Coil | 1806 | 0 / 1
4425 | Al_ActiveExhFan_15 |  | BOOL |  | Coil | 1807 | 0 / 1
4424 | Al_ActiveSupFan_2 |  | BOOL |  | Coil | 1808 | 0 / 1
4423 | Al_ActiveSupFan_3 |  | BOOL |  | Coil | 1809 | 0 / 1
4422 | Al_ActiveSupFan_4 |  | BOOL |  | Coil | 1810 | 0 / 1
4421 | Al_ActiveExhFan_2 |  | BOOL |  | Coil | 1811 | 0 / 1
4420 | Al_ActiveExhFan_3 |  | BOOL |  | Coil | 1812 | 0 / 1
4419 | Al_ActiveExhFan_4 |  | BOOL |  | Coil | 1813 | 0 / 1
4418 | Al_ActiveSupFan_5 |  | BOOL |  | Coil | 1814 | 0 / 1
4417 | Al_ActiveSupFan_6 |  | BOOL |  | Coil | 1815 | 0 / 1
4416 | Al_ActiveSupFan_7 |  | BOOL |  | Coil | 1816 | 0 / 1
4415 | Al_ActiveSupFan_8 |  | BOOL |  | Coil | 1817 | 0 / 1
4414 | Al_ActiveSupFan_9 |  | BOOL |  | Coil | 1818 | 0 / 1
4413 | Al_ActiveExhFan_5 |  | BOOL |  | Coil | 1819 | 0 / 1
4412 | Al_ActiveExhFan_6 |  | BOOL |  | Coil | 1820 | 0 / 1
4411 | Al_ActiveExhFan_7 |  | BOOL |  | Coil | 1821 | 0 / 1
4410 | Al_ActiveExhFan_8 |  | BOOL |  | Coil | 1822 | 0 / 1
4409 | Al_ActiveExhFan_9 |  | BOOL |  | Coil | 1823 | 0 / 1
4408 | Al_ActiveRotary |  | BOOL |  | Coil | 1824 | 0 / 1
4407 | FanTempReg_2 |  | Bool |  | Coil | 1825 | 0 / 1
4406 | Pressure3_Simulation_En |  | Bool |  | Coil | 1826 | 0 / 1
4405 | Pressure4_Simulation_En |  | Bool |  | Coil | 1827 | 0 / 1
4404 | Pressure5_Simulation_En |  | Bool |  | Coil | 1828 | 0 / 1
4403 | Add_Online_1 |  | Bool |  | Coil | 1829 | 0 / 1
4402 | Add_Online_2 |  | Bool |  | Coil | 1830 | 0 / 1
4401 | Add_Online_3 |  | Bool |  | Coil | 1831 | 0 / 1
4400 | Add_En_1 |  | Bool |  | Coil | 1832 | 0 / 1
4399 | Add_En_2 |  | Bool |  | Coil | 1833 | 0 / 1
4398 | Add_En_3 |  | Bool |  | Coil | 1834 | 0 / 1
4397 | MB_Set_Start_Addr |  | Bool |  | Coil | 1835 | 0 / 1
4396 | MB_Set_Start_Par |  | Bool |  | Coil | 1836 | 0 / 1
4395 | MB_Set_Start_Pass |  | Bool |  | Coil | 1837 | 0 / 1
4394 | MB_Set_Start_Read |  | Bool |  | Coil | 1838 | 0 / 1
4393 | MB_Set_Start_Test |  | Bool |  | Coil | 1839 | 0 / 1
4392 | MB_Set_Start |  | Bool |  | Coil | 1840 | 0 / 1
4391 | MB_FanSupply_En_1 |  | Bool |  | Coil | 1841 | 0 / 1
4390 | MB_FanSupply_En_2 |  | Bool |  | Coil | 1842 | 0 / 1
4389 | MB_FanSupply_En_3 |  | Bool |  | Coil | 1843 | 0 / 1
4388 | MB_FanSupply_En_4 |  | Bool |  | Coil | 1844 | 0 / 1
4387 | MB_FanSupply_En_5 |  | Bool |  | Coil | 1845 | 0 / 1
4386 | MB_FanSupply_En_6 |  | Bool |  | Coil | 1846 | 0 / 1
4385 | MB_FanSupply_En_7 |  | Bool |  | Coil | 1847 | 0 / 1
4384 | MB_FanSupply_En_8 |  | Bool |  | Coil | 1848 | 0 / 1
4383 | MB_FanSupply_En_9 |  | Bool |  | Coil | 1849 | 0 / 1
4382 | MB_FanSupply_En_10 |  | Bool |  | Coil | 1850 | 0 / 1
4381 | MB_FanReturn_En_1 |  | Bool |  | Coil | 1851 | 0 / 1
4380 | MB_FanReturn_En_2 |  | Bool |  | Coil | 1852 | 0 / 1
4379 | MB_FanReturn_En_3 |  | Bool |  | Coil | 1853 | 0 / 1
4378 | MB_FanReturn_En_4 |  | Bool |  | Coil | 1854 | 0 / 1
4377 | MB_FanReturn_En_5 |  | Bool |  | Coil | 1855 | 0 / 1
4376 | MB_FanReturn_En_6 |  | Bool |  | Coil | 1856 | 0 / 1
4375 | MB_FanReturn_En_7 |  | Bool |  | Coil | 1857 | 0 / 1
4374 | MB_FanReturn_En_8 |  | Bool |  | Coil | 1858 | 0 / 1
4373 | MB_FanReturn_En_9 |  | Bool |  | Coil | 1859 | 0 / 1
4372 | MB_FanReturn_En_10 |  | Bool |  | Coil | 1860 | 0 / 1
4371 | StartupJmp |  | Bool |  | Coil | 1861 | 0 / 1
4370 | AlrmActive |  | Bool |  | Coil | 1862 | 0 / 1
4369 | Scheduler_OnOffUnit.Scheduler_1.DaySchedActive |  | Bool |  | Coil | 1863 | 0 / 1
4368 | Scheduler_OnOffUnit.Scheduler_1.VacationActive |  | Bool |  | Coil | 1864 | 0 / 1
4367 | Scheduler_OnOffUnit.Scheduler_1.SpecDayActive |  | Bool |  | Coil | 1865 | 0 / 1
4366 | UnitToBeConfigured |  | Bool |  | Coil | 1866 | 0 / 1
3475 | AppCool_CW | SYS - Application Code - Cooling coil [0 / 1] | Bool | ReadWrite | Coil | 2001 | 0 / 1 | 0 - NO 1 - YES
3476 | AppCool_DX | SYS - Application Code - Direct Expansion [0 / 1] | Bool | ReadWrite | Coil | 2002 | 0 / 1 | 0 - NO 1 - YES
3477 | AppEco | SYS - Application Code - Mixing damper [0 / 1] | Bool | ReadWrite | Coil | 2003 | 0 / 1 | 0 - NO 1 - YES
3478 | AppHeat_DX | SYS - Application Code - Heat - Direct Expansion [0 / 1] | Bool | ReadWrite | Coil | 2004 | 0 / 1 | 0 - NO 1 - YES
3479 | AppHeat_HE | SYS - Application Code - Electric Heating [0 / 1] | Bool | ReadWrite | Coil | 2005 | 0 / 1 | 0 - NO 1 - YES
3480 | AppHeat_HW | SYS - Application Code - Heating Coil [0 / 1] | Bool | ReadWrite | Coil | 2006 | 0 / 1 | 0 - NO 1 - YES
3481 | AppHeat_Steam | SYS - Application Code - Heating Steam [0 / 1] | Bool | ReadWrite | Coil | 2007 | 0 / 1 | 0 - NO 1 - YES
3482 | AppHum_Evap | SYS - Application Code - Humidity - Evap [0 / 1] | Bool | ReadWrite | Coil | 2008 | 0 / 1 | 0 - NO 1 - YES
3483 | AppHum_Steam | SYS - Application Code - Humidity - Steam [0 / 1] | Bool | ReadWrite | Coil | 2009 | 0 / 1 | 0 - NO 1 - YES
3484 | AppPreHeat_DX | SYS - Application Code - PreHeat_DX [0 / 1] | Bool | ReadWrite | Coil | 2010 | 0 / 1 | 0 - NO 1 - YES
3485 | AppPreHeat_HE | SYS - Application Code - PreHeat_HE [0 / 1] | Bool | ReadWrite | Coil | 2011 | 0 / 1 | 0 - NO 1 - YES
3486 | AppPreHeat_HW | SYS - Application Code - PreHeat_HW [0 / 1] | Bool | ReadWrite | Coil | 2012 | 0 / 1 | 0 - NO 1 - YES
3487 | AppRec_EnExh | SYS - Application Code - Return [0 / 1] | Bool | ReadWrite | Coil | 2013 | 0 / 1 | 0 - NO 1 - YES
3488 | AppRec_Glycol | SYS - Application Code - Rec_Glycol [0 / 1] | Bool | ReadWrite | Coil | 2014 | 0 / 1 | 0 - NO 1 - YES
3489 | AppRec_Plate | SYS - Application Code - Rec_Plate [0 / 1] | Bool | ReadWrite | Coil | 2015 | 0 / 1 | 0 - NO 1 - YES
3490 | AppRec_Rotary | SYS - Application Code - Recovery - Rotary [0 / 1] | Bool | ReadWrite | Coil | 2016 | 0 / 1 | 0 - NO 1 - YES
3491 | AppRec_SupplyOnly | SYS - Application Code - Rec_SupplyOnly [0 / 1] | Bool | ReadWrite | Coil | 2017 | 0 / 1 | 0 - NO 1 - YES
3492 | AppReg_Ret | SYS - Application Code - Reg_Ret [0 / 1] | Bool | ReadWrite | Coil | 2018 | 0 / 1 | 0 - NO 1 - YES
3493 | AppReg_Room | SYS - Application Code - Reg_Room [0 / 1] | Bool | ReadWrite | Coil | 2019 | 0 / 1 | 0 - NO 1 - YES
3494 | AppReg_Supply | SYS - Application Code - Reg_Supply [0 / 1] | Bool | ReadWrite | Coil | 2020 | 0 / 1 | 0 - NO 1 - YES
3495 | AppReHeat_DX | SYS - Application Code - ReHeat_DX [0 / 1] | Bool | ReadWrite | Coil | 2021 | 0 / 1 | 0 - NO 1 - YES
3496 | AppReHeat_HE | SYS - Application Code - ReHeat_HE [0 / 1] | Bool | ReadWrite | Coil | 2022 | 0 / 1 | 0 - NO 1 - YES
3497 | AppReHeat_HW | SYS - Application Code - ReHeat_HW [0 / 1] | Bool | ReadWrite | Coil | 2023 | 0 / 1 | 0 - NO 1 - YES
3498 | AppRev_DX | SYS - Application Code - Rev_DX [0 / 1] | Bool | ReadWrite | Coil | 2024 | 0 / 1 | 0 - NO 1 - YES
3499 | AppRev_W | SYS - Application Code - Rev_W [0 / 1] | Bool | ReadWrite | Coil | 2025 | 0 / 1 | 0 - NO 1 - YES
3500 | AppRevCoolDX | SYS - Application Code - RevCoolDX [0 / 1] | Bool | ReadWrite | Coil | 2026 | 0 / 1 | 0 - NO 1 - YES
3501 | AppRevCoolW | SYS - Application Code - RevCoolW [0 / 1] | Bool | ReadWrite | Coil | 2027 | 0 / 1 | 0 - NO 1 - YES
3502 | AppRevHeatDX | SYS - Application Code - RevHeatDX [0 / 1] | Bool | ReadWrite | Coil | 2028 | 0 / 1 | 0 - NO 1 - YES
3503 | AppRevHeatW | SYS - Application Code - RevHeatW [0 / 1] | Bool | ReadWrite | Coil | 2029 | 0 / 1 | 0 - NO 1 - YES
3504 | BacNetSel | SYS - Unit Configuration - BacNet Port [0 / 1] | Bool | ReadWrite | Coil | 2030 | 0 / 1 | 0 - ETHERNET 1 - PLAN
3505 | CO2_Simulation_En | SYS - IO Setting - CO2 Simulate - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2031 | 0 / 1 | 0 - NO 1 - YES
3506 | CoolAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Cool [0 / 1] | Bool | ReadWrite | Coil | 2032 | 0 / 1 | 0 - NC 1 - NO
3507 | En_Buzz | SYS - Unit Configuration - Enable Buzzer [0 / 1] | Bool | ReadWrite | Coil | 2033 | 0 / 1 | 0 - NO 1 - YES
3508 | En_HumTHTN_1 | SYS - Unit Configuration - HMI Basic - Humidity Probe [0 / 1] | Bool | ReadWrite | Coil | 2034 | 0 / 1 | 0 - NO 1 - YES
3509 | En_RetAir_CO2 | SYS - IO Setting - Enable Modbus - CO2 [0 / 1] | Bool | ReadWrite | Coil | 2035 | 0 / 1 | 0 - NO 1 - YES
3510 | En_RetAirP | SYS - IO Setting - Enable Modbus - Pressure - Return [0 / 1] | Bool | ReadWrite | Coil | 2036 | 0 / 1 | 0 - NO 1 - YES
3511 | En_RetHum | SYS - IO Setting - Enable Modbus - Humidity - Return [0 / 1] | Bool | ReadWrite | Coil | 2037 | 0 / 1 | 0 - NO 1 - YES
3512 | En_SupplyAirP | SYS - IO Setting - Enable Modbus - Pressure - Supply [0 / 1] | Bool | ReadWrite | Coil | 2038 | 0 / 1 | 0 - NO 1 - YES
3513 | En_SupplyHum | SYS - IO Setting - Enable Modbus - Humidity - Supply [0 / 1] | Bool | ReadWrite | Coil | 2039 | 0 / 1 | 0 - NO 1 - YES
3514 | ExhAirDamp.Logic | SYS - IO Setting - Digital Output - Logic - Damper - Supply [0 / 1] | Bool | ReadWrite | Coil | 2040 | 0 / 1 | 0 - NC 1 - NO
3515 | ExtTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - External [0 / 1] | Bool | ReadWrite | Coil | 2041 | 0 / 1 | 0 - NO 1 - YES
3516 | FireAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm Fire [0 / 1] | Bool | ReadWrite | Coil | 2042 | 0 / 1 | 0 - NC 1 - NO
3517 | Heat_2.Logic | SYS - IO Setting - Digital Output - Logic - Heating 2 [0 / 1] | Bool | ReadWrite | Coil | 2043 | 0 / 1 | 0 - NC 1 - NO
3518 | HumAlrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Humidifier [0 / 1] | Bool | ReadWrite | Coil | 2044 | 0 / 1 | 0 - NC 1 - NO
3519 | ID2_Alrm.Logic | SYS - IO Setting - Digital Input - Logic - Alarm - Heat [0 / 1] | Bool | ReadWrite | Coil | 2045 | 0 / 1 | 0 - NC 1 - NO
3520 | RecSupplyTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Supply Recovery [0 / 1] | Bool | ReadWrite | Coil | 2046 | 0 / 1 | 0 - NO 1 - YES
3521 | RemoteOn.Logic | SYS - IO Setting - Digital Input - Logic - Remote ON [0 / 1] | Bool | ReadWrite | Coil | 2047 | 0 / 1 | 0 - NC 1 - NO
3522 | RetFilter.Logic | SYS - IO Setting - Digital Input - Logic - Filter - Return [0 / 1] | Bool | ReadWrite | Coil | 2048 | 0 / 1 | 0 - NC 1 - NO
3523 | RetTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Return [0 / 1] | Bool | ReadWrite | Coil | 2049 | 0 / 1 | 0 - NO 1 - YES
3524 | SrsAlrm.Logic | SYS - IO Setting - Digital Output - Logic - Global Alarm [0 / 1] | Bool | ReadWrite | Coil | 2050 | 0 / 1 | 0 - NC 1 - NO
3525 | SupplyFilter.Logic | SYS - IO Setting - Digital Input - Logic - Filter - Supply [0 / 1] | Bool | ReadWrite | Coil | 2051 | 0 / 1 | 0 - NC 1 - NO
3526 | UnitConfigured | SYS - Unit Configuration - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2052 | 0 / 1 | 0 - NO 1 - YES
3527 | W_HeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Water Heat [0 / 1] | Bool | ReadWrite | Coil | 2053 | 0 / 1 | 0 - NO 1 - YES
3528 | W_PreHeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - Water PreHeat [0 / 1] | Bool | ReadWrite | Coil | 2054 | 0 / 1 | 0 - NO 1 - YES
3529 | WinSum.Enabled | SYS - IO Setting - Enable Inputs - Summer / Winter [0 / 1] | Bool | ReadWrite | Coil | 2055 | 0 / 1 | 0 - NO 1 - YES
3530 | WinSum.Logic | SYS - IO Setting - Digital Input - Logic - Winter / Summer [0 / 1] | Bool | ReadWrite | Coil | 2056 | 0 / 1 | 0 - NC 1 - NO
3531 | CurrVer.IsBeta | SYS - System - Application Version - _ . _ . _ _ _ B _ _ | Bool | Read | Coil | 2057
3532 | ExhTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature Exhaust [0 / 1] | Bool | Read | Coil | 2058 | 0 / 1 | 0 - NO 1 - YES
3533 | Manual_PreHeat | SYS - PreHeater - Manual mode active [0 / 1] | Bool | Read | Coil | 2059 | 0 / 1 | 0 - NO 1 - YES
3534 | Manual_Recovery | SYS - Recovery - Manual mode active [0 / 1] | Bool | Read | Coil | 2060 | 0 / 1 | 0 - NO 1 - YES
3535 | Manual_Heat | SYS - Heater - Manual mode active [0 / 1] | Bool | Read | Coil | 2061 | 0 / 1 | 0 - NO 1 - YES
3536 | Manual_Cool | SYS - Cooler - Manual mode active [0 / 1] | Bool | Read | Coil | 2062 | 0 / 1 | 0 - NO 1 - YES
3537 | Manual_ReHeat | SYS - ReHeater - Manual mode active [0 / 1] | Bool | Read | Coil | 2063 | 0 / 1 | 0 - NO 1 - YES
3538 | Manual_Reverse | SYS - Reverse unit - Manual mode active [0 / 1] | Bool | Read | Coil | 2064 | 0 / 1 | 0 - NO 1 - YES
3539 | Manual_Mix | SYS - Mixing damper - Manual mode active [0 / 1] | Bool | Read | Coil | 2065 | 0 / 1 | 0 - NO 1 - YES
3540 | Manual_Humidity | SYS - Humidifier - Manual mode active [0 / 1] | Bool | Read | Coil | 2066 | 0 / 1 | 0 - NO 1 - YES
3541 | Manual_RedDamp | SYS - Redundant Damper - Manual mode active [0 / 1] | Bool | Read | Coil | 2067 | 0 / 1 | 0 - NO 1 - YES
3542 | Manual_Active |  | Bool |  | Coil | 2068 | 0 / 1
3543 | QR_En_Compact_CBX |  | Bool |  | Coil | 2069 | 0 / 1
3544 | QR_En_Compact_RRG |  | Bool |  | Coil | 2070 | 0 / 1
3545 | QR_En_Compact_HEX |  | Bool |  | Coil | 2071 | 0 / 1
3546 | En_IO_PCB |  | Bool |  | Coil | 2072 | 0 / 1
3547 | En_MainBoard |  | Bool |  | Coil | 2073 | 0 / 1
3548 | Fire_AutoReset_En |  | Bool |  | Coil | 2074 | 0 / 1
3549 | Pres_Filtr_En |  | Bool |  | Coil | 2075 | 0 / 1
3550 | Pressure1_Simulation_En |  | Bool |  | Coil | 2076 | 0 / 1
3551 | Pressure2_Simulation_En |  | Bool |  | Coil | 2077 | 0 / 1
3552 | SupHum_Simulation_En |  | Bool |  | Coil | 2078 | 0 / 1
3553 | RetHum_Simulation_En |  | Bool |  | Coil | 2079 | 0 / 1
3554 | En_SupplyAirP_2 |  | Bool |  | Coil | 2080 | 0 / 1
3555 | En_SupplyAirP_3 |  | Bool |  | Coil | 2081 | 0 / 1
3556 | En_RetAirP_2 |  | Bool |  | Coil | 2082 | 0 / 1
3557 | PreHTempReg |  | Bool |  | Coil | 2083 | 0 / 1
3558 | DoubleDamp.Val | IO - Digital Output - Damper - Redundant [0 / 1] | Bool | Read | Coil | 2084 | 0 / 1 | 0 - ON 1 - OFF
3559 | DoubleDamp.Logic |  | Bool |  | Coil | 2085 | 0 / 1
3560 | DoubleDamp.Enabled |  | Bool |  | Coil | 2086 | 0 / 1
3561 | En_MainBoard_TempHumid |  | Bool |  | Coil | 2087 | 0 / 1
3562 | En_MainBoard_Humid |  | Bool |  | Coil | 2088 | 0 / 1
3563 | En_MainBoard_PressSup |  | Bool |  | Coil | 2089 | 0 / 1
3564 | En_MainBoard_PressRet |  | Bool |  | Coil | 2090 | 0 / 1
3565 | En_MainBoard_Filter |  | Bool |  | Coil | 2091 | 0 / 1
3566 | UnitToBeConfigured |  | Bool |  | Coil | 2092 | 0 / 1
3567 | AfterPreHeatCoilTemp.Enabled | SYS - IO Setting - Enable Inputs - Temperature - After PreHeat [0 / 1] | Bool | ReadWrite | Coil | 2093 | 0 / 1 | 0 - NO 1 - YES
3568 | EnDate | CLK - Time - Setting - Change Enable [0 / 1] | Bool | ReadWrite | Coil | 2094 | 0 / 1 | 0 - NO 1 - YES
3569 | UnitCoolHeatMode | MO - Unit - Cooling / Heating [0 / 1] | Bool | ReadWrite | Coil | 2095 | 0 / 1 | 0 - Cooling 1 - Heating
3570 | MixAirDamp_On | MO - Damper Mixing - On [0 / 1] | Bool | Read | Coil | 2096 | 0 / 1
3571 | RunExhFan | MO - Fan - Return - On [0 / 1] | Bool | Read | Coil | 2097 | 0 / 1
3572 | RunSupplyFan | MO - Fan - Supply - On [0 / 1] | Bool | Read | Coil | 2098 | 0 / 1
3573 | UnitOff | MO - Unit - On [0 / 1] | Bool | Read | Coil | 2099 | 0 / 1
3574 | UnitOn | MO - Unit - Off [0 / 1] | Bool | Read | Coil | 2100 | 0 / 1
3876 | ExpEn |  | Bool | ReadWrite | Coil | 2101 | 0 / 1 | 1 - Enable export to DEV file
3877 | ImpEn |  | Bool | ReadWrite | Coil | 2102 | 0 / 1 | 1 - Enable import form DEV file
3575 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Enabled | SCH - Scheduller - Monday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2151 | 0 / 1 | 0 - OFF 1 - ON
3576 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Flag_Enabled | SCH - Scheduller - Monday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2152 | 0 / 1
3577 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Enabled | SCH - Scheduller - Monday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2153 | 0 / 1 | 0 - OFF 1 - ON
3578 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Flag_Enabled | SCH - Scheduller - Monday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2154 | 0 / 1
3579 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Enabled | SCH - Scheduller - Monday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2155 | 0 / 1 | 0 - OFF 1 - ON
3580 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Flag_Enabled | SCH - Scheduller - Monday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2156 | 0 / 1
3581 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Enabled | SCH - Scheduller - Monday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2157 | 0 / 1 | 0 - OFF 1 - ON
3582 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Flag_Enabled | SCH - Scheduller - Monday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2158 | 0 / 1
3583 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Enabled | SCH - Scheduller - Tuesday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2159 | 0 / 1 | 0 - OFF 1 - ON
3584 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Flag_Enabled | SCH - Scheduller - Tuesday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2160 | 0 / 1
3585 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Enabled | SCH - Scheduller - Tuesday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2161 | 0 / 1 | 0 - OFF 1 - ON
3586 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Flag_Enabled | SCH - Scheduller - Tuesday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2162 | 0 / 1
3587 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Enabled | SCH - Scheduller - Tuesday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2163 | 0 / 1 | 0 - OFF 1 - ON
3588 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Flag_Enabled | SCH - Scheduller - Tuesday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2164 | 0 / 1
3589 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Enabled | SCH - Scheduller - Tuesday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2165 | 0 / 1 | 0 - OFF 1 - ON
3590 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Flag_Enabled | SCH - Scheduller - Tuesday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2166 | 0 / 1
3591 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Enabled | SCH - Scheduller - Wednesday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2167 | 0 / 1 | 0 - OFF 1 - ON
3592 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Flag_Enabled | SCH - Scheduller - Wednesday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2168 | 0 / 1
3593 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Enabled | SCH - Scheduller - Wednesday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2169 | 0 / 1 | 0 - OFF 1 - ON
3594 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Flag_Enabled | SCH - Scheduller - Wednesday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2170 | 0 / 1
3595 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Enabled | SCH - Scheduller - Wednesday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2171 | 0 / 1 | 0 - OFF 1 - ON
3596 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Flag_Enabled | SCH - Scheduller - Wednesday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2172 | 0 / 1
3597 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Enabled | SCH - Scheduller - Wednesday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2173 | 0 / 1 | 0 - OFF 1 - ON
3598 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Flag_Enabled | SCH - Scheduller - Wednesday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2174 | 0 / 1
3599 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Enabled | SCH - Scheduller - Thursday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2175 | 0 / 1 | 0 - OFF 1 - ON
3600 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Flag_Enabled | SCH - Scheduller - Thursday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2176 | 0 / 1
3601 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Enabled | SCH - Scheduller - Thursday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2177 | 0 / 1 | 0 - OFF 1 - ON
3602 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Flag_Enabled | SCH - Scheduller - Thursday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2178 | 0 / 1
3603 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Enabled | SCH - Scheduller - Thursday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2179 | 0 / 1 | 0 - OFF 1 - ON
3604 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Flag_Enabled | SCH - Scheduller - Thursday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2180 | 0 / 1
3605 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Enabled | SCH - Scheduller - Thursday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2181 | 0 / 1 | 0 - OFF 1 - ON
3606 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Flag_Enabled | SCH - Scheduller - Thursday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2182 | 0 / 1
3607 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Enabled | SCH - Scheduller - Friday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2183 | 0 / 1 | 0 - OFF 1 - ON
3608 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Flag_Enabled | SCH - Scheduller - Friday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2184 | 0 / 1
3609 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Enabled | SCH - Scheduller - Friday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2185 | 0 / 1 | 0 - OFF 1 - ON
3610 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Flag_Enabled | SCH - Scheduller - Friday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2186 | 0 / 1
3611 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Enabled | SCH - Scheduller - Friday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2187 | 0 / 1 | 0 - OFF 1 - ON
3612 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Flag_Enabled | SCH - Scheduller - Friday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2188 | 0 / 1
3613 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Enabled | SCH - Scheduller - Friday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2189 | 0 / 1 | 0 - OFF 1 - ON
3614 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Flag_Enabled | SCH - Scheduller - Friday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2190 | 0 / 1
3615 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Enabled | SCH - Scheduller - Saturday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2191 | 0 / 1 | 0 - OFF 1 - ON
3616 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Flag_Enabled | SCH - Scheduller - Saturday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2192 | 0 / 1
3617 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Enabled | SCH - Scheduller - Saturday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2193 | 0 / 1 | 0 - OFF 1 - ON
3618 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Flag_Enabled | SCH - Scheduller - Saturday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2194 | 0 / 1
3619 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Enabled | SCH - Scheduller - Saturday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2195 | 0 / 1 | 0 - OFF 1 - ON
3620 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Flag_Enabled | SCH - Scheduller - Saturday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2196 | 0 / 1
3621 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Enabled | SCH - Scheduller - Saturday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2197 | 0 / 1 | 0 - OFF 1 - ON
3622 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Flag_Enabled | SCH - Scheduller - Saturday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2198 | 0 / 1
3623 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Enabled | SCH - Scheduller - Sunday - 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2199 | 0 / 1 | 0 - OFF 1 - ON
3624 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Flag_Enabled | SCH - Scheduller - Sunday - 1 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2200 | 0 / 1
3625 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Enabled | SCH - Scheduller - Sunday - 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2201 | 0 / 1 | 0 - OFF 1 - ON
3626 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Flag_Enabled | SCH - Scheduller - Sunday - 2 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2202 | 0 / 1
3627 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Enabled | SCH - Scheduller - Sunday - 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2203 | 0 / 1 | 0 - OFF 1 - ON
3628 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Flag_Enabled | SCH - Scheduller - Sunday - 3 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2204 | 0 / 1
3629 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Enabled | SCH - Scheduller - Sunday - 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2205 | 0 / 1 | 0 - OFF 1 - ON
3630 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Flag_Enabled | SCH - Scheduller - Sunday - 4 - Flag_Enabled [0 / 1] | Bool | ReadWrite | Coil | 2206 | 0 / 1
3631 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].Enabled | SCH - Scheduller - Special Days 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2207 | 0 / 1 | 0 - OFF 1 - ON
3632 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].Enabled | SCH - Scheduller - Special Days 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2208 | 0 / 1 | 0 - OFF 1 - ON
3633 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].Enabled | SCH - Scheduller - Special Days 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2209 | 0 / 1 | 0 - OFF 1 - ON
3634 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].Enabled | SCH - Scheduller - Special Days 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2210 | 0 / 1 | 0 - OFF 1 - ON
3635 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].Enabled | SCH - Scheduller - Special Days 5 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2211 | 0 / 1 | 0 - OFF 1 - ON
3636 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].Enabled | SCH - Scheduller - Special Days 6 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2212 | 0 / 1 | 0 - OFF 1 - ON
3637 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Enabled | SCH - Scheduller - Time Band 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2213 | 0 / 1 | 0 - OFF 1 - ON
3638 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Enabled | SCH - Scheduller - Time Band 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2214 | 0 / 1 | 0 - OFF 1 - ON
3639 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Enabled | SCH - Scheduller - Time Band 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2215 | 0 / 1 | 0 - OFF 1 - ON
3640 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Enabled | SCH - Scheduller - Time Band 4 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2216 | 0 / 1 | 0 - OFF 1 - ON
3641 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].Enabled | SCH - Scheduller - Periods 1 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2217 | 0 / 1 | 0 - OFF 1 - ON
3642 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].Enabled | SCH - Scheduller - Periods 2 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2218 | 0 / 1 | 0 - OFF 1 - ON
3643 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].Enabled | SCH - Scheduller - Periods 3 - Enabled [0 / 1] | Bool | ReadWrite | Coil | 2219 | 0 / 1 | 0 - OFF 1 - ON
3644 | SchedActive | SCH - Scheduller - Active [0 / 1] | Bool | Read | Coil | 2220 | 0 / 1 | 0 - NO 1 - YES
3645 | Scheduler_OnOffUnit.Scheduler_1.DaySchedActive |  | Bool | ReadWrite | Coil | 2221 | 0 / 1
3646 | Scheduler_OnOffUnit.Scheduler_1.VacationActive |  | Bool | ReadWrite | Coil | 2222 | 0 / 1
3647 | Scheduler_OnOffUnit.Scheduler_1.SpecDayActive |  | Bool | ReadWrite | Coil | 2223 | 0 / 1
3648 | SchedOn | SCH - Scheduller - On [0 / 1] | Bool | ReadWrite | Coil | 2224 | 0 / 1 | 0 - OFF 1 - ON
3649 | Cool_1.Logic | PAR - Cooling - Main Cooler - Logic [0 / 1] | Bool | ReadWrite | Coil | 2301 | 0 / 1 | 0 - NC 1 - NO
3650 | Cool_2.Logic | PAR - Cooling - Main Cooler DX - Logic [0 / 1] | Bool | ReadWrite | Coil | 2302 | 0 / 1 | 0 - NC 1 - NO
3651 | En_CoolRec | PAR - Recovery - Cooling - Enable [0 / 1] | Bool | ReadWrite | Coil | 2303 | 0 / 1 | 0 - NO 1 - YES
3652 | En_FreeCoolHeat | PAR - System - Free Cool/Heat - Enable [0 / 1] | Bool | ReadWrite | Coil | 2304 | 0 / 1 | 0 - NO 1 - YES
3653 | En_Rev_MixDamper | PAR - Mixing damper - Reverse signal [0 / 1] | Bool | ReadWrite | Coil | 2305 | 0 / 1 | 0 - NO 1 - YES
3654 | En_Rev_Recovery | PAR - Recovery - Reverse signal [0 / 1] | Bool | ReadWrite | Coil | 2306 | 0 / 1 | 0 - NO 1 - YES
3655 | FastHeatEn | PAR - Recovery - Fast Heating - Enable [0 / 1] | Bool | ReadWrite | Coil | 2307 | 0 / 1 | 0 - NO 1 - YES
3656 | FastHeatStop | PAR - Recovery - Stop Fast Heat - Enable [0 / 1] | Bool | ReadWrite | Coil | 2308 | 0 / 1 | 0 - NO 1 - YES
3657 | FastHeatTrig | PAR - Recovery - Start Fast Heat - Enable [0 / 1] | Bool | ReadWrite | Coil | 2309 | 0 / 1 | 0 - NO 1 - YES
3658 | HC_Cool_1.Res | PAR - Cooling - Main Cooler - Reset [0 / 1] | Bool | ReadWrite | Coil | 2310 | 0 / 1 | 0 - NO 1 - YES
3659 | HC_Cool_2.Res | PAR - Cooling - Main Cooler DX - Reset [0 / 1] | Bool | ReadWrite | Coil | 2311 | 0 / 1 | 0 - NO 1 - YES
3660 | HC_ExhFan_1.Res | PAR - Fan - Return 1 - Reset [0 / 1] | Bool | ReadWrite | Coil | 2312 | 0 / 1 | 0 - NO 1 - YES
3661 | HC_ExhFan_2.Res | PAR - Fan - Return 2 - Reset [0 / 1] | Bool | ReadWrite | Coil | 2313 | 0 / 1 | 0 - NO 1 - YES
3662 | HC_Heat_1.Res | PAR - Heating - Main Heater - Reset [0 / 1] | Bool | ReadWrite | Coil | 2314 | 0 / 1 | 0 - NO 1 - YES
3663 | HC_Heat_2.Res | PAR - Heating - Main Device 2 - Reset [0 / 1] | Bool | ReadWrite | Coil | 2315 | 0 / 1 | 0 - NO 1 - YES
3664 | HC_Hum.Res | PAR - Humidity - Reset [0 / 1] | Bool | ReadWrite | Coil | 2316 | 0 / 1 | 0 - NO 1 - YES
3665 | HC_PreHeat.Res | PAR - Heating - PreHeating - Reset [0 / 1] | Bool | ReadWrite | Coil | 2317 | 0 / 1 | 0 - NO 1 - YES
3666 | HC_RecoveryPump.Res | PAR - Recovery - Reset [0 / 1] | Bool | ReadWrite | Coil | 2318 | 0 / 1 | 0 - NO 1 - YES
3667 | HC_ReHeat.Res | PAR - Heating - ReHeating - Reset [0 / 1] | Bool | ReadWrite | Coil | 2319 | 0 / 1 | 0 - NO 1 - YES
3668 | HC_SupplyFan_1.Res | PAR - Fan - Supply 1 - Reset [0 / 1] | Bool | ReadWrite | Coil | 2320 | 0 / 1 | 0 - NO 1 - YES
3669 | HC_SupplyFan_2.Res | PAR - Fan - Supply 2 - Reset [0 / 1] | Bool | ReadWrite | Coil | 2321 | 0 / 1 | 0 - NO 1 - YES
3670 | Heat_1.Logic | PAR - Heating - Main Heater - Logic [0 / 1] | Bool | ReadWrite | Coil | 2322 | 0 / 1 | 0 - NC 1 - NO
3671 | Hum.Logic | PAR - Humidity - Logic [0 / 1] | Bool | ReadWrite | Coil | 2323 | 0 / 1 | 0 - NC 1 - NO
3672 | PreHeaterPump.Logic | PAR - Heating - PreHeating - Logic [0 / 1] | Bool | ReadWrite | Coil | 2324 | 0 / 1 | 0 - NC 1 - NO
3673 | RecoveryPump.Logic | PAR - Recovery - Logic [0 / 1] | Bool | ReadWrite | Coil | 2325 | 0 / 1 | 0 - NC 1 - NO
3674 | ReHeat.Logic | PAR - Heating - ReHeating - Logic [0 / 1] | Bool | ReadWrite | Coil | 2326 | 0 / 1 | 0 - NC 1 - NO
3675 | RevOut_1.Logic | PAR - Heating - Reverse Device 1 - Logic [0 / 1] | Bool | ReadWrite | Coil | 2327 | 0 / 1 | 0 - NC 1 - NO
3676 | RevOut_2.Logic | PAR - Heating - Reverse Device 2 - Logic [0 / 1] | Bool | ReadWrite | Coil | 2328 | 0 / 1 | 0 - NC 1 - NO
3677 | LowSupplyTemp_Off | PAR - Heating - Supply Limit - Threshold unit STOP [0 / 1] | Bool | ReadWrite | Coil | 2329 | 0 / 1 | 0 - NO 1 - YES
3678 | PreHeat_Always | PAR - Heating - Main Heater HW - Pre-Heat always start [0 / 1] | Bool | ReadWrite | Coil | 2330 | 0 / 1 | 0 - NO 1 - YES
3679 | DoubleFanRot_Manual | PAR - Fan - Redundant - Manual rotation [0 / 1] | Bool | ReadWrite | Coil | 2331 | 0 / 1 | 0 - NO 1 - YES
3680 | FanTempReg | PAR - Fan - Temperature regulation - Enable [0 / 1] | Bool | ReadWrite | Coil | 2332 | 0 / 1 | 0 - NO 1 - YES
3681 | RRG_0_10V | PAR - Recovery - Rotery - Enable 0-10V on Y3 for RRG [0 / 1] | Bool | ReadWrite | Coil | 2333 | 0 / 1 | 0 - NO 1 - YES
3682 | En_RRG_Alarm | PAR - Recovery - Rotery - Alarm enable [0 / 1] | Bool | ReadWrite | Coil | 2334 | 0 / 1 | 0 - NO 1 - YES
3683 | Mix_Mode_ECO | PAR - Mixing - Manual mode ECO - Enable [0 / 1] | Bool | ReadWrite | Coil | 2335 | 0 / 1 | 0 - NO 1 - YES
3684 | Mix_Mode_OPTIMAL | PAR - Mixing - Manual mode Optimal - Enable [0 / 1] | Bool | ReadWrite | Coil | 2336 | 0 / 1 | 0 - NO 1 - YES
3685 | Mix_Mode_COMFORT | PAR - Mixing - Manual mode Comfort - Enable [0 / 1] | Bool | ReadWrite | Coil | 2337 | 0 / 1 | 0 - NO 1 - YES
3686 | FanTempReg_2 |  | Bool | ReadWrite | Coil | 2338 | 0 / 1
3687 | Res_Filter_Counter |  | Bool | ReadWrite | Coil | 2339 | 0 / 1
3688 | MB_Devices.MB_MainBoard_1.Zeroing_En |  | Bool | ReadWrite | Coil | 2340 | 0 / 1
3689 | MB_Rev_Press_Fan |  | Bool | ReadWrite | Coil | 2341 | 0 / 1
3690 | MB_Rev_Press_Filter |  | Bool | ReadWrite | Coil | 2342 | 0 / 1
3691 | En_Fan_AI |  | Bool | ReadWrite | Coil | 2343 | 0 / 1
3692 | En_Basic_Res |  | Bool | ReadWrite | Coil | 2344 | 0 / 1
3693 | MB_Devices.IO_PCB_1.IN1 |  | Bool | ReadWrite | Coil | 2345 | 0 / 1
3694 | MB_Devices.IO_PCB_1.IN2 |  | Bool | ReadWrite | Coil | 2346 | 0 / 1
3695 | Pressure3_Simulation_En |  | Bool | ReadWrite | Coil | 2347 | 0 / 1
3696 | Pressure4_Simulation_En |  | Bool | ReadWrite | Coil | 2348 | 0 / 1
3697 | Pressure5_Simulation_En |  | Bool | ReadWrite | Coil | 2349 | 0 / 1
3698 | Add_Online_1 |  | Bool | ReadWrite | Coil | 2350 | 0 / 1
3699 | Add_Online_2 |  | Bool | ReadWrite | Coil | 2351 | 0 / 1
3700 | Add_Online_3 |  | Bool | ReadWrite | Coil | 2352 | 0 / 1
3701 | Add_En_1 |  | Bool | ReadWrite | Coil | 2353 | 0 / 1
3702 | Add_En_2 |  | Bool | ReadWrite | Coil | 2354 | 0 / 1
3703 | Add_En_3 |  | Bool | ReadWrite | Coil | 2355 | 0 / 1
3704 | MB_Set_Start_Addr |  | Bool | ReadWrite | Coil | 2356 | 0 / 1
3705 | MB_Set_Start_Par |  | Bool | ReadWrite | Coil | 2357 | 0 / 1
3706 | MB_Set_Start_Pass |  | Bool | ReadWrite | Coil | 2358 | 0 / 1
3707 | MB_Set_Start_Read |  | Bool | ReadWrite | Coil | 2359 | 0 / 1
3708 | MB_Set_Start_Test |  | Bool | ReadWrite | Coil | 2360 | 0 / 1
3709 | MB_Set_Start |  | Bool | ReadWrite | Coil | 2361 | 0 / 1
3710 | StartupJmp |  | Bool | ReadWrite | Coil | 2362 | 0 / 1
3880 | En_Cycle_Res |  | Bool | ReadWrite | Coil | 2363 | 0 / 1
3881 | En_THTN_1 |  | Bool | ReadWrite | Coil | 2364 | 0 / 1
3711 | MB_FanSupply_En_1 |  | Bool |  | Coil | 3001 | 0 / 1
3712 | MB_FanSupply_En_2 |  | Bool |  | Coil | 3002 | 0 / 1
3713 | MB_FanSupply_En_3 |  | Bool |  | Coil | 3003 | 0 / 1
3714 | MB_FanSupply_En_4 |  | Bool |  | Coil | 3004 | 0 / 1
3715 | MB_FanSupply_En_5 |  | Bool |  | Coil | 3005 | 0 / 1
3716 | MB_FanSupply_En_6 |  | Bool |  | Coil | 3006 | 0 / 1
3717 | MB_FanSupply_En_7 |  | Bool |  | Coil | 3007 | 0 / 1
3718 | MB_FanSupply_En_8 |  | Bool |  | Coil | 3008 | 0 / 1
3719 | MB_FanSupply_En_9 |  | Bool |  | Coil | 3009 | 0 / 1
3720 | MB_FanSupply_En_10 |  | Bool |  | Coil | 3010 | 0 / 1
3721 | MB_FanSupply_En_11 |  | Bool |  | Coil | 3011 | 0 / 1
3722 | MB_FanSupply_En_12 |  | Bool |  | Coil | 3012 | 0 / 1
3723 | MB_FanSupply_En_13 |  | Bool |  | Coil | 3013 | 0 / 1
3724 | MB_FanSupply_En_14 |  | Bool |  | Coil | 3014 | 0 / 1
3725 | MB_FanSupply_En_15 |  | Bool |  | Coil | 3015 | 0 / 1
3726 | MB_FanReturn_En_1 |  | Bool |  | Coil | 3016 | 0 / 1
3727 | MB_FanReturn_En_2 |  | Bool |  | Coil | 3017 | 0 / 1
3728 | MB_FanReturn_En_3 |  | Bool |  | Coil | 3018 | 0 / 1
3729 | MB_FanReturn_En_4 |  | Bool |  | Coil | 3019 | 0 / 1
3730 | MB_FanReturn_En_5 |  | Bool |  | Coil | 3020 | 0 / 1
3731 | MB_FanReturn_En_6 |  | Bool |  | Coil | 3021 | 0 / 1
3732 | MB_FanReturn_En_7 |  | Bool |  | Coil | 3022 | 0 / 1
3733 | MB_FanReturn_En_8 |  | Bool |  | Coil | 3023 | 0 / 1
3734 | MB_FanReturn_En_9 |  | Bool |  | Coil | 3024 | 0 / 1
3735 | MB_FanReturn_En_10 |  | Bool |  | Coil | 3025 | 0 / 1
3736 | MB_FanReturn_En_11 |  | Bool |  | Coil | 3026 | 0 / 1
3737 | MB_FanReturn_En_12 |  | Bool |  | Coil | 3027 | 0 / 1
3738 | MB_FanReturn_En_13 |  | Bool |  | Coil | 3028 | 0 / 1
3739 | MB_FanReturn_En_14 |  | Bool |  | Coil | 3029 | 0 / 1
3740 | MB_FanReturn_En_15 |  | Bool |  | Coil | 3030 | 0 / 1
3741 | En_Exh_VAV |  | Bool |  | Coil | 3031 | 0 / 1
3742 | En_Exh_CAV |  | Bool |  | Coil | 3032 | 0 / 1
3743 | En_EC_2 |  | Bool |  | Coil | 3033 | 0 / 1
3744 | En_ExhFan_2 |  | Bool |  | Coil | 3034 | 0 / 1
3745 | ExhMulti_3 |  | Bool |  | Coil | 3035 | 0 / 1
3746 | ExhMulti_4 |  | Bool |  | Coil | 3036 | 0 / 1
3747 | ExhMulti_5 |  | Bool |  | Coil | 3037 | 0 / 1
3748 | ExhMulti_6 |  | Bool |  | Coil | 3038 | 0 / 1
3749 | ExhMulti_7 |  | Bool |  | Coil | 3039 | 0 / 1
3750 | ExhMulti_8 |  | Bool |  | Coil | 3040 | 0 / 1
3751 | ExhMulti_9 |  | Bool |  | Coil | 3041 | 0 / 1
3752 | ExhMulti_10 |  | Bool |  | Coil | 3042 | 0 / 1
3753 | ExhMulti_11 |  | Bool |  | Coil | 3043 | 0 / 1
3754 | ExhMulti_12 |  | Bool |  | Coil | 3044 | 0 / 1
3755 | ExhMulti_13 |  | Bool |  | Coil | 3045 | 0 / 1
3756 | ExhMulti_14 |  | Bool |  | Coil | 3046 | 0 / 1
3757 | ExhMulti_15 |  | Bool |  | Coil | 3047 | 0 / 1
3758 | ExhMulti_2 |  | Bool |  | Coil | 3048 | 0 / 1
3759 | En_Supply_VAV |  | Bool |  | Coil | 3049 | 0 / 1
3760 | En_Supply_CAV |  | Bool |  | Coil | 3050 | 0 / 1
3761 | En_EC |  | Bool |  | Coil | 3051 | 0 / 1
3762 | En_SupplyFan_2 |  | Bool |  | Coil | 3052 | 0 / 1
3763 | SupplyMulti_2 |  | Bool |  | Coil | 3053 | 0 / 1
3764 | SupplyMulti_3 |  | Bool |  | Coil | 3054 | 0 / 1
3765 | SupplyMulti_4 |  | Bool |  | Coil | 3055 | 0 / 1
3766 | SupplyMulti_5 |  | Bool |  | Coil | 3056 | 0 / 1
3767 | SupplyMulti_6 |  | Bool |  | Coil | 3057 | 0 / 1
3768 | SupplyMulti_7 |  | Bool |  | Coil | 3058 | 0 / 1
3769 | SupplyMulti_8 |  | Bool |  | Coil | 3059 | 0 / 1
3770 | SupplyMulti_9 |  | Bool |  | Coil | 3060 | 0 / 1
3771 | SupplyMulti_10 |  | Bool |  | Coil | 3061 | 0 / 1
3772 | SupplyMulti_11 |  | Bool |  | Coil | 3062 | 0 / 1
3773 | SupplyMulti_12 |  | Bool |  | Coil | 3063 | 0 / 1
3774 | SupplyMulti_13 |  | Bool |  | Coil | 3064 | 0 / 1
3775 | SupplyMulti_14 |  | Bool |  | Coil | 3065 | 0 / 1
3776 | SupplyMulti_15 |  | Bool |  | Coil | 3066 | 0 / 1
3777 | MultiRed |  | Bool |  | Coil | 3067 | 0 / 1
3778 | SupplyMultiRed |  | Bool |  | Coil | 3068 | 0 / 1
3779 | ExhMultiRed |  | Bool |  | Coil | 3069 | 0 / 1
3780 | Online_VFD_Set |  | Bool |  | Coil | 3070 | 0 / 1
3781 | CoolAlrm.Val | IO - Digital Input - Cooler - Alarm [0 / 1] | Bool | Read | Coil | 3701 | 0 / 1
3782 | RetFilter.Val | IO - Digital Input - Filter - Return [0 / 1] | Bool | Read | Coil | 3702 | 0 / 1
3783 | SupplyFilter.Val | IO - Digital Input - Filter - Supply [0 / 1] | Bool | Read | Coil | 3703 | 0 / 1
3784 | FireAlrm.Val | IO - Digital Input - Fire - Alarm [0 / 1] | Bool | Read | Coil | 3704 | 0 / 1
3785 | ID2_Alrm.Val | IO - Digital Input - Freeze - Alarm [0 / 1] | Bool | Read | Coil | 3705 | 0 / 1
3786 | HumAlrm.Val | IO - Digital Input - Humidifier - Alarm [0 / 1] | Bool | Read | Coil | 3706 | 0 / 1
3787 | RemoteOn.Val | IO - Digital Input - Remote - ON [0 / 1] | Bool | Read | Coil | 3707 | 0 / 1
3788 | WinSum.Val | IO - Digital Input - Winter / Summer [0 / 1] | Bool | Read | Coil | 3708 | 0 / 1
3789 | Alarm_Val_DO |  | Bool |  | Coil | 3709 | 0 / 1
3790 | Cool_1_Val_DO |  | Bool |  | Coil | 3710 | 0 / 1
3791 | Cool_2_Val_DO |  | Bool |  | Coil | 3711 | 0 / 1
3792 | Damper_Val_DO |  | Bool |  | Coil | 3712 | 0 / 1
3793 | Heat_1_Val_DO |  | Bool |  | Coil | 3713 | 0 / 1
3794 | Heat_2_Val_DO |  | Bool |  | Coil | 3714 | 0 / 1
3795 | CoolHeat_Val_DO |  | Bool |  | Coil | 3715 | 0 / 1
3796 | Humid_Val_DO |  | Bool |  | Coil | 3716 | 0 / 1
3797 | PreHeat_Val_DO |  | Bool |  | Coil | 3717 | 0 / 1
3798 | Recovery_Val_DO |  | Bool |  | Coil | 3718 | 0 / 1
3799 | Redundant_Val_DO |  | Bool |  | Coil | 3719 | 0 / 1
3800 | ReHeat_Val_DO |  | Bool |  | Coil | 3720 | 0 / 1
3801 | RevOut_1_Val_DO |  | Bool |  | Coil | 3721 | 0 / 1
3802 | RevOut_2_Val_DO |  | Bool |  | Coil | 3722 | 0 / 1
3803 | Cool_1.HW_Val |  | Bool |  | Coil | 3723 | 0 / 1
4001 | Al_Offline_Rotary.Active | AL - Alarm - Rotary - Offline [0 / 1] | Bool | Read | Coil | 4001 | 0 / 1
3804 | Al_HeatCoilTempPrb.Active | AL - Alarm - Probe - Temperature Water Heating coil [0 / 1] | Bool | Read | Coil | 4002 | 0 / 1
3805 | Al_ExtTempPrb.Active | AL - Alarm - Probe - Temperature External [0 / 1] | Bool | Read | Coil | 4003 | 0 / 1
3806 | Al_ExhTempPrb.Active | AL - Alarm - Probe - Temperature Exhaust [0 / 1] | Bool | Read | Coil | 4004 | 0 / 1
3807 | Al_Offline_SP_ExhHum.Active | AL - Alarm - Probe - Return Humidity - Offline [0 / 1] | Bool | Read | Coil | 4005 | 0 / 1
3808 | Al_Offline_SP_ExhPress.Active | AL - Alarm - Probe - Return Air Pressure - Offline [0 / 1] | Bool | Read | Coil | 4006 | 0 / 1
3809 | Al_LowSupplyTemp.Active | AL - Alarm - Probe - Low Supply Temperature [0 / 1] | Bool | Read | Coil | 4007 | 0 / 1
3810 | Al_AfterPreHeatCoilTempPrb.Active | AL - Alarm - Probe - After preheating coil temperature [0 / 1] | Bool | Read | Coil | 4008 | 0 / 1
3811 | Al_Offline_SP_SupplyHum.Active | AL - Alarm - Probe - Supply humidity - Offline [0 / 1] | Bool | Read | Coil | 4009 | 0 / 1
3812 | Al_Offline_SP_SupplyPress.Active | AL - Alarm - Probe - Supply Air Pressure - Offline [0 / 1] | Bool | Read | Coil | 4010 | 0 / 1
3813 | Al_HumWorkHrsWarn.Active | AL - Alarm - Humidity - Works Hour Warning [0 / 1] | Bool | Read | Coil | 4011 | 0 / 1
3814 | Al_Hum.Active | AL - Alarm - Humidifier [0 / 1] | Bool | Read | Coil | 4012 | 0 / 1
3815 | Al_Heat.Active | AL - Alarm - Heating - Device Alarm [0 / 1] | Bool | Read | Coil | 4013 | 0 / 1
3816 | Al_HeatExchgWorkHrsWarn.Active | AL - Alarm - HeatExchanger - HeatExchanger Works Hour Warning [0 / 1] | Bool | Read | Coil | 4014 | 0 / 1
3817 | Al_Fire.Active | AL - Alarm - Fire [0 / 1] | Bool | Read | Coil | 4015 | 0 / 1
3818 | Al_FireExh.Active | AL - Alarm - Fire - Return Temperature [0 / 1] | Bool | Read | Coil | 4016 | 0 / 1
3819 | Al_Offline_ExhFan_1.Active | AL - Alarm - Fan Return 1 - Offline [0 / 1] | Bool | Read | Coil | 4017 | 0 / 1
3820 | Al_Err_retain_write.Active | AL - Alarm - Error retain write [0 / 1] | Bool | Read | Coil | 4018 | 0 / 1
3821 | Al_Cool.Active | AL - Alarm - Cooling - Device Alarm [0 / 1] | Bool | Read | Coil | 4019 | 0 / 1
3822 | Al_MB_Temperature.Active | AL - Alarm - Control Circuit - Temperature [0 / 1] | Bool | Read | Coil | 4020 | 0 / 1
3823 | Al_MB_Temp_Filter_Supply.Active | AL - Alarm - Control Circuit - Temp_Filter_Supply [0 / 1] | Bool | Read | Coil | 4021 | 0 / 1
3824 | Al_MB_Temp_Filter_Return.Active | AL - Alarm - Control Circuit - Temp_Filter_Return [0 / 1] | Bool | Read | Coil | 4022 | 0 / 1
3825 | Al_MB_Temp_Fan_Supply.Active | AL - Alarm - Control Circuit - Temp_Fan_Supply [0 / 1] | Bool | Read | Coil | 4023 | 0 / 1
3826 | Al_MB_Temp_Fan_Return.Active | AL - Alarm - Control Circuit - Temp_Fan_Return [0 / 1] | Bool | Read | Coil | 4024 | 0 / 1
3827 | Al_MB_Supply24.Active | AL - Alarm - Control Circuit - Supply24 [0 / 1] | Bool | Read | Coil | 4025 | 0 / 1
3828 | Al_MB_Press_Filter_Supply.Active | AL - Alarm - Control Circuit - Press_Filter_Supply [0 / 1] | Bool | Read | Coil | 4026 | 0 / 1
3829 | Al_MB_Press_Filter_Return.Active | AL - Alarm - Control Circuit - Press_Filter_Return [0 / 1] | Bool | Read | Coil | 4027 | 0 / 1
3830 | Al_MB_Press_Fan_Supply.Active | AL - Alarm - Control Circuit - Press_Fan_Supply [0 / 1] | Bool | Read | Coil | 4028 | 0 / 1
3831 | Al_MB_Press_Fan_Return.Active | AL - Alarm - Control Circuit - Press_Fan_Return [0 / 1] | Bool | Read | Coil | 4029 | 0 / 1
3832 | Al_Offline_MainBoard.Active | AL - Alarm - Control Circuit - Offline [0 / 1] | Bool | Read | Coil | 4030 | 0 / 1
3833 | Al_MB_Humidity.Active | AL - Alarm - Control Circuit - Humidity [0 / 1] | Bool | Read | Coil | 4031 | 0 / 1
3834 | Al_MB_Control_Temp.Active | AL - Alarm - Control Circuit - Control_Temp [0 / 1] | Bool | Read | Coil | 4032 | 0 / 1
3835 | Al_MB_Control_Supply.Active | AL - Alarm - Control Circuit - Control_Supply [0 / 1] | Bool | Read | Coil | 4033 | 0 / 1
3836 | Al_MB_AO4.Active | AL - Alarm - Control Circuit - AO4 [0 / 1] | Bool | Read | Coil | 4034 | 0 / 1
3837 | Al_MB_AO3.Active | AL - Alarm - Control Circuit - AO3 [0 / 1] | Bool | Read | Coil | 4035 | 0 / 1
3838 | Al_MB_AO2.Active | AL - Alarm - Control Circuit - AO2 [0 / 1] | Bool | Read | Coil | 4036 | 0 / 1
3839 | Al_MB_AO1_AO4_PWM.Active | AL - Alarm - Control Circuit - AO1_AO4_PWM [0 / 1] | Bool | Read | Coil | 4037 | 0 / 1
3840 | Al_MB_AO1.Active | AL - Alarm - Control Circuit - AO1 [0 / 1] | Bool | Read | Coil | 4038 | 0 / 1
3841 | Al_Offline_cpCOe.Active | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | Bool | Read | Coil | 4039 | 0 / 1
3842 | Al_CfgError_cpCOe.Active | AL - Alarm - Module IO - cPCOE - Configuration error [0 / 1] | Bool | Read | Coil | 4040 | 0 / 1
3843 | AlarmMng.AlrmResByBms | AL - Alarm - BMS - Reset [0 / 1] | Bool | ReadWrite | Coil | 4041 | 0 / 1 | 0 - 1 - RESET
3844 | Al_BMS_Offline.Active | AL - Alarm - BMS - Offline [0 / 1] | Bool | Read | Coil | 4042 | 0 / 1
3845 | Al_AFreezePreHeatPRB.Active | AL - Alarm - Antifreeze - PreHeat Back Water Temperature [0 / 1] | Bool | Read | Coil | 4043 | 0 / 1
3846 | Al_AFreezeDIN.Active | AL - Alarm - Antifreeze - Digital Input [0 / 1] | Bool | Read | Coil | 4044 | 0 / 1
3847 | Al_AFreezePRB.Active | AL - Alarm - Antifreeze - Back Water Temperature [0 / 1] | Bool | Read | Coil | 4045 | 0 / 1
3848 | Al_PreHeatCoilTempPrb.Active | AL - Alarm - Probe - Temperature Water PreHeating Coil [0 / 1] | Bool | Read | Coil | 4046 | 0 / 1
3849 | Al_RDT_Fan.Active | AL - Alarm - Fan Group [0 / 1] | Bool | Read | Coil | 4047 | 0 / 1
3850 | Al_RecSupplyTemp.Active | AL - Alarm - Probe - Supply Recovery Temperature [0 / 1] | Bool | Read | Coil | 4048 | 0 / 1
3851 | Al_ReheatCoilWorkHrsWarn.Active | AL - Alarm - ReHeatCoil - Works Hour Warning [0 / 1] | Bool | Read | Coil | 4049 | 0 / 1
3852 | Al_retain.Active | AL - Alarm - Retain [0 / 1] | Bool | Read | Coil | 4050 | 0 / 1
3853 | Al_RetAir_CO2_Lev_Prb.Active | AL - Alarm - Probe - CO2 Return Level Probe [0 / 1] | Bool | Read | Coil | 4051 | 0 / 1
3854 | Al_RetAirFlwSwWarn.Active | AL - Alarm - Probe - Air Flow Return SW Warning [0 / 1] | Bool | Read | Coil | 4052 | 0 / 1
3855 | Al_RetAirP_Prb.Active | AL - Alarm - Probe - Pressure Return Air [0 / 1] | Bool | Read | Coil | 4053 | 0 / 1
3856 | Al_RetFanWorkHrsWarn.Active | AL - Alarm - Fan Return - Works Hour Warning [0 / 1] | Bool | Read | Coil | 4054 | 0 / 1
3857 | Al_RetFilt.Active | AL - Alarm - Filter - Return [0 / 1] | Bool | Read | Coil | 4055 | 0 / 1
3858 | Al_RetTempPrb.Active | AL - Alarm - Probe - Return Temperature [0 / 1] | Bool | Read | Coil | 4056 | 0 / 1
3859 | Al_SupplyAirFlwSwWarn.Active | AL - Alarm - Probe - Supply Air Flow SW Warning [0 / 1] | Bool | Read | Coil | 4057 | 0 / 1
3860 | Al_SupplyAirP_Prb.Active | AL - Alarm - Probe - Supply Air Pressure [0 / 1] | Bool | Read | Coil | 4058 | 0 / 1
3861 | Al_SupplyFanWorkHrsWarn.Active | AL - Alarm - Fan Supply - Works Hour Warning [0 / 1] | Bool | Read | Coil | 4059 | 0 / 1
3862 | Al_SupplyFilt.Active | AL - Alarm - Filter - Supply [0 / 1] | Bool | Read | Coil | 4060 | 0 / 1
3863 | Al_SupplyTempPrb.Active | AL - Alarm - Probe - Supply Temperature [0 / 1] | Bool | Read | Coil | 4061 | 0 / 1
3864 | Al_SwPrototype.Active | AL - Alarm - Software Version - Prototype [0 / 1] | Bool | Read | Coil | 4062 | 0 / 1
3865 | CfgErrAlrm.Active | AL - Alarm - Device - Wrong configuration [0 / 1] | Bool | Read | Coil | 4063 | 0 / 1
3866 | Al_MotorFault_EC_ExhFan1.Active | AL - Alarm - Fan Return 1 EC - Motor Fault [0 / 1] | Bool | Read | Coil | 4064 | 0 / 1
3867 | OfflineAlrm.Active | AL - Alarm - Device - Offline [0 / 1] | Bool | Read | Coil | 4065 | 0 / 1
3868 | Al_Offline_IO_PCB.Active | AL - Alarm - Module IO - EC-PCB - Offline [0 / 1] | Bool | Read | Coil | 4066 | 0 / 1
3869 | Al_DXRev.Active | AL - Alarm - Reverse unit [0 / 1] | Bool | Read | Coil | 4067 | 0 / 1
3870 | Al_WarningFilterHigh.Active | AL - Alarm - Filter - High pressure [0 / 1] | Bool | Read | Coil | 4068 | 0 / 1
3871 | Al_RRG_WorkConfirm.Active | AL - Alarm - Recovery - Rotary - Work confirm [0 / 1] | Bool | Read | Coil | 4069 | 0 / 1
3872 | CfgErrAlrm_CPCOE_1.Active | AL - Alarm - Module IO - cPCOE - Configuration [0 / 1] | Bool | Read | Coil | 4070 | 0 / 1
3873 | OfflineAlrm_CPCOE_1.Active | AL - Alarm - Module IO - cPCOE - Offline [0 / 1] | Bool | Read | Coil | 4071 | 0 / 1
3874 | Filter_Counter_Al |  | Bool |  | Coil | 4072
3875 | AlrmActive |  | Bool |  | Coil | 4073
4002 | Al_HP_Alarm.Active | Heat Pump Alarm | Bool |  | Coil | 4100 | 0 / 1
4003 | Al_HP_Offline.Active | Heat Pump Alarm | Bool |  | Coil | 4101 | 0 / 1
4004 | Al_BLT_M_Alarm.Active | Heat Pump Alarm | Bool |  | Coil | 4102 | 0 / 1
4005 | comstatus.Active | Heat Pump Alarm | Bool |  | Coil | 4103 | 0 / 1
4006 | HP_Al_EmergencyClosing_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4104 | 0 / 1
4007 | HP_Al_LowSH_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4105 | 0 / 1
4008 | HP_Al_LOP_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4106 | 0 / 1
4009 | HP_Al_MOP_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4107 | 0 / 1 | Alarm status
4010 | HP_Al_EEV_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4108 | 0 / 1 | Alarm status
4011 | HP_Al_LowSuct_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4109 | 0 / 1 | Alarm status
4012 | HP_Al_HiTempCond_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4110 | 0 / 1 | Alarm status
4013 | HP_Al_RangeError_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4111 | 0 / 1 | Alarm status
4014 | HP_Al_PinOutOfBound_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4112 | 0 / 1 | Alarm status
4015 | HP_mAl_retain.Active | Heat Pump Alarm | Bool |  | Coil | 4113 | 0 / 1 | Alarm status
4016 | HP_mAl_Err_retain_write.Active | Heat Pump Alarm | Bool |  | Coil | 4114 | 0 / 1 | Alarm status
4017 | HP_Al_DscgPrbP.Active | Heat Pump Alarm | Bool |  | Coil | 4115 | 0 / 1 | Alarm status
4018 | HP_Al_SuctPrbP.Active | Heat Pump Alarm | Bool |  | Coil | 4116 | 0 / 1 | Alarm status
4019 | HP_Al_DscgPrbTemp.Active | Heat Pump Alarm | Bool |  | Coil | 4117 | 0 / 1 | Alarm status
4020 | HP_Al_SuctPrbTemp.Active | Heat Pump Alarm | Bool |  | Coil | 4118 | 0 / 1 | Alarm status
4021 | HP_Al_RefSpeed.Active | Heat Pump Alarm | Bool |  | Coil | 4119 | 0 / 1 | Alarm status
4022 | HP_Al_DisStartDpState_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4120 | 0 / 1 | Alarm status
4023 | HP_Al_OutEnv_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4121 | 0 / 1 | Alarm status
4024 | HP_Al_StartFailRetry_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4122 | 0 / 1 | Alarm status
4025 | HP_Al_StartFailLock_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4123 | 0 / 1 | Alarm status
4026 | HP_Al_LowDeltaP_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4124 | 0 / 1 | Alarm status
4027 | HP_Al_HighDscgT_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4125 | 0 / 1 | Alarm status
4028 | HP_Al01_DriveOverCurrent_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4126 | 0 / 1 | Alarm status
4029 | HP_Al02_MotorOvld_IsqT_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4127 | 0 / 1 | Alarm status
4030 | HP_Al03_DC_BusOverVolt_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4128 | 0 / 1 | Alarm status
4031 | HP_Al04_DC_BusUnderVolt_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4129 | 0 / 1 | Alarm status
4032 | HP_Al05_DriveOverTemp_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4130 | 0 / 1 | Alarm status
4033 | HP_Al06_DriveUnderTemp_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4131 | 0 / 1 | Alarm status
4034 | HP_Al07_HW_OverCurrent_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4132 | 0 / 1 | Alarm status
4035 | HP_Al08_PTC_MotOverTemp_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4133 | 0 / 1 | Alarm status
4036 | HP_Al09_DriveOutputFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4134 | 0 / 1 | Alarm status
4037 | HP_Al10_FlashDataErr_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4135 | 0 / 1 | Alarm status
4038 | HP_Al11_ParamDef_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4136 | 0 / 1 | Alarm status
4039 | HP_Al12_DC_RippleTooLarge_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4137 | 0 / 1 | Alarm status
4040 | HP_Al13_MB_CommLost_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4138 | 0 / 1 | Alarm status
4041 | HP_Al14_DriveThermistorFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4139 | 0 / 1 | Alarm status
4042 | HP_Al15_AutotuneFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4140 | 0 / 1 | Alarm status
4043 | HP_Al16_DriveDis_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4141 | 0 / 1 | Alarm status
4044 | HP_Al17_MotPhLoss_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4142 | 0 / 1 | Alarm status
4045 | HP_Al18_FanFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4143 | 0 / 1 | Alarm status
4046 | HP_Al19_SpeedFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4144 | 0 / 1 | Alarm status
4047 | HP_Al20_PFC_Failure_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4145 | 0 / 1 | Alarm status
4048 | HP_Al21_PFC_OverVolt_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4146 | 0 / 1 | Alarm status
4049 | HP_Al22_PFC_UnderVolt_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4147 | 0 / 1 | Alarm status
4050 | HP_Al23_STO_Survey01_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4148 | 0 / 1 | Alarm status
4051 | HP_Al24_STO_Survey02_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4149 | 0 / 1 | Alarm status
4052 | HP_Al25_GroundFault_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4150 | 0 / 1 | Alarm status
4053 | HP_Al26_ADC_ConvSync_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4151 | 0 / 1 | Alarm status
4054 | HP_Al27_HW_Sync_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4152 | 0 / 1 | Alarm status
4055 | HP_Al28_DriveOvld_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4153 | 0 / 1 | Alarm status
4056 | HP_Al29_uCSaf_DriveStop_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4154 | 0 / 1 | Alarm status
4057 | HP_Al98_UnexpectedRestart_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4155 | 0 / 1 | Alarm status
4058 | HP_Al99_UnexpectedStop_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4156 | 0 / 1 | Alarm status
4059 | HP_Al_InvOffline_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4157 | 0 / 1 | Alarm status
4060 | HP_Al_LiqdPrbT.Active | Heat Pump Alarm | Bool |  | Coil | 4158 | 0 / 1 | Alarm status
4061 | HP_Al_AuxPrb_A.Active | Heat Pump Alarm | Bool |  | Coil | 4159 | 0 / 1 | Alarm status
4062 | HP_Al_AuxPrb_B.Active | Heat Pump Alarm | Bool |  | Coil | 4160 | 0 / 1 | Alarm status
4063 | HP_Al_AuxPrb_C.Active | Heat Pump Alarm | Bool |  | Coil | 4161 | 0 / 1 | Alarm status
4064 | HP_Al_BmsOffline.Active | Heat Pump Alarm | Bool |  | Coil | 4162 | 0 / 1 | Alarm status
4065 | HP_Al_Comp2Fault.Active | Heat Pump Alarm | Bool |  | Coil | 4163 | 0 / 1 | Alarm status
4066 | HP_Al_Comp3Fault.Active | Heat Pump Alarm | Bool |  | Coil | 4164 | 0 / 1 | Alarm status
4067 | HP_Al_SelfTuning_A_EVD.Active | Heat Pump Alarm | Bool |  | Coil | 4165 | 0 / 1 | Alarm status
4068 | HP_AlSafe101_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4166 | 0 / 1 | Alarm status
4069 | HP_AlSafe102_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4167 | 0 / 1 | Alarm status
4070 | HP_AlSafe103_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4168 | 0 / 1 | Alarm status
4071 | HP_AlSafe104_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4169 | 0 / 1 | Alarm status
4072 | HP_AlSafe105_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4170 | 0 / 1 | Alarm status
4073 | HP_AlSafe106_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4171 | 0 / 1 | Alarm status
4074 | HP_AlSafe107_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4172 | 0 / 1 | Alarm status
4075 | HP_AlSafe108_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4173 | 0 / 1 | Alarm status
4076 | HP_AlSafe109_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4174 | 0 / 1 | Alarm status
4077 | HP_AlSafe110_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4175 | 0 / 1 | Alarm status
4078 | HP_AlSafe111_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4176 | 0 / 1 | Alarm status
4079 | HP_AlSafe112_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4177 | 0 / 1 | Alarm status
4080 | HP_AlSafe113_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4178 | 0 / 1 | Alarm status
4081 | HP_AlSafe114_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4179 | 0 / 1 | Alarm status
4082 | HP_AlSafe115_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4180 | 0 / 1 | Alarm status
4083 | HP_AlSafe116_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4181 | 0 / 1 | Alarm status
4084 | HP_AlSafe201_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4182 | 0 / 1 | Alarm status
4085 | HP_AlSafe202_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4183 | 0 / 1 | Alarm status
4086 | HP_AlSafe203_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4184 | 0 / 1 | Alarm status
4087 | HP_AlSafe204_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4185 | 0 / 1 | Alarm status
4088 | HP_AlSafe205_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4186 | 0 / 1 | Alarm status
4089 | HP_AlSafe206_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4187 | 0 / 1 | Alarm status
4090 | HP_AlSafe207_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4188 | 0 / 1 | Alarm status
4091 | HP_AlSafe208_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4189 | 0 / 1 | Alarm status
4092 | HP_AlSafe209_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4190 | 0 / 1 | Alarm status
4093 | HP_AlSafe210_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4191 | 0 / 1 | Alarm status
4094 | HP_AlSafe211_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4192 | 0 / 1 | Alarm status
4095 | HP_AlSafe212_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4193 | 0 / 1 | Alarm status
4096 | HP_AlSafe213_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4194 | 0 / 1 | Alarm status
4097 | HP_AlSafe214_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4195 | 0 / 1 | Alarm status
4098 | HP_AlSafe215_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4196 | 0 / 1 | Alarm status
4099 | HP_AlSafe216_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4197 | 0 / 1 | Alarm status
4100 | HP_Al_ComprOff_BLDC1.Active | Heat Pump Alarm | Bool |  | Coil | 4198 | 0 / 1 | Alarm status
4101 | HP_AlEnv02_HighRatio_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4199 | 0 / 1 | Alarm status
4102 | HP_AlEnv03_HighDscg_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4200 | 0 / 1 | Alarm status
4103 | HP_AlEnv04_HighCurr_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4201 | 0 / 1 | Alarm status
4104 | HP_AlEnv05_HighSuct_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4202 | 0 / 1 | Alarm status
4105 | HP_AlEnv06_LowRatio_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4203 | 0 / 1 | Alarm status
4106 | HP_ALEnv07_LowDP_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4204 | 0 / 1 | Alarm status
4107 | HP_AlEnv08_LowDscg_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4205 | 0 / 1 | Alarm status
4108 | HP_AlEnv09_LowSuct_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4206 | 0 / 1 | Alarm status
4109 | HP_AlEnv10_HDT_BLDC_1.Active | Heat Pump Alarm | Bool |  | Coil | 4207 | 0 / 1 | Alarm status
4110 | HP_Al_SuctPrbTemp_VapInj.Active | Heat Pump Alarm | Bool |  | Coil | 4208 | 0 / 1 | Alarm status
4111 | HP_Al_SuctPrbP_VapInj.Active | Heat Pump Alarm | Bool |  | Coil | 4209 | 0 / 1 | Alarm status
4112 | HP_Al_EvapPrbTemp_VapInj.Active | Heat Pump Alarm | Bool |  | Coil | 4210 | 0 / 1 | Alarm status
4113 | HP_Al_ExtPrbTemp.Active | Heat Pump Alarm | Bool |  | Coil | 4211 | 0 / 1 | Alarm status
4114 | HP_Al_Low_SH_A_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4212 | 0 / 1 | Alarm status
4115 | HP_Al_Low_SH_B_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4213 | 0 / 1 | Alarm status
4116 | HP_Al_LOP_A_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4214 | 0 / 1 | Alarm status
4117 | HP_Al_LOP_B_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4215 | 0 / 1 | Alarm status
4118 | HP_Al_MOP_A_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4216 | 0 / 1 | Alarm status
4119 | HP_Al_MOP_B_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4217 | 0 / 1 | Alarm status
4120 | HP_Al_EEV_A_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4218 | 0 / 1 | Alarm status
4121 | HP_Al_EEV_B_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4219 | 0 / 1 | Alarm status
4122 | HP_Al_LowSuct_A_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4220 | 0 / 1 | Alarm status
4123 | HP_Al_LowSuct_B_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4221 | 0 / 1 | Alarm status
4124 | HP_Al_HiT_Cond_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4222 | 0 / 1 | Alarm status
4125 | HP_Al_S1_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4223 | 0 / 1 | Alarm status
4126 | HP_Al_S2_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4224 | 0 / 1 | Alarm status
4127 | HP_Al_S3_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4225 | 0 / 1 | Alarm status
4128 | HP_Al_S4_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4226 | 0 / 1 | Alarm status
4129 | HP_Al_Batt_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4227 | 0 / 1 | Alarm status
4130 | HP_Al_EEPROM_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4228 | 0 / 1 | Alarm status
4131 | HP_Al_IncompleteClosing_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4229 | 0 / 1 | Alarm status
4132 | HP_Al_EmergencyClosing_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4230 | 0 / 1 | Alarm status
4133 | HP_Al_FW_CompatibErr_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4231 | 0 / 1 | Alarm status
4134 | HP_Al_ConfigErr_EVD_1.Active | Heat Pump Alarm | Bool |  | Coil | 4232 | 0 / 1 | Alarm status
4135 | HP_Al_EVD_EVO_1_Offline.Active | Heat Pump Alarm | Bool |  | Coil | 4233 | 0 / 1 | Alarm status
4136 | HP_Al01_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4234 | 0 / 1 | Alarm status
4137 | HP_Al02_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4235 | 0 / 1 | Alarm status
4138 | HP_Al03_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4236 | 0 / 1 | Alarm status
4139 | HP_Al04_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4237 | 0 / 1 | Alarm status
4140 | HP_Al05_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4238 | 0 / 1 | Alarm status
4141 | HP_Al06_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4239 | 0 / 1 | Alarm status
4142 | HP_Al07_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4240 | 0 / 1 | Alarm status
4143 | HP_Al08_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4241 | 0 / 1 | Alarm status
4144 | HP_Al09_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4242 | 0 / 1 | Alarm status
4145 | HP_Al10_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4243 | 0 / 1 | Alarm status
4146 | HP_Al11_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4244 | 0 / 1 | Alarm status
4147 | HP_Al12_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4245 | 0 / 1 | Alarm status
4148 | HP_Al13_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4246 | 0 / 1 | Alarm status
4149 | HP_Al14_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4247 | 0 / 1 | Alarm status
4150 | HP_Al15_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4248 | 0 / 1 | Alarm status
4151 | HP_Al16_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4249 | 0 / 1 | Alarm status
4152 | HP_Al17_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4250 | 0 / 1 | Alarm status
4153 | HP_Al18_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4251 | 0 / 1 | Alarm status
4154 | HP_Al19_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4252 | 0 / 1 | Alarm status
4155 | HP_Al20_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4253 | 0 / 1 | Alarm status
4156 | HP_Al21_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4254 | 0 / 1 | Alarm status
4157 | HP_Al22_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4255 | 0 / 1 | Alarm status
4158 | HP_Al23_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4256 | 0 / 1 | Alarm status
4159 | HP_Al24_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4257 | 0 / 1 | Alarm status
4160 | HP_Al25_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4258 | 0 / 1 | Alarm status
4161 | HP_Al26_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4259 | 0 / 1 | Alarm status
4162 | HP_Al27_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4260 | 0 / 1 | Alarm status
4163 | HP_Al28_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4261 | 0 / 1 | Alarm status
4164 | HP_Al29_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4262 | 0 / 1 | Alarm status
4165 | HP_Al98_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4263 | 0 / 1 | Alarm status
4166 | HP_Al99_PWRP_1.Active | Heat Pump Alarm | Bool |  | Coil | 4264 | 0 / 1 | Alarm status
1 | AfterPreHeatCoilTemp.Val | IO - Probe - Temperature - After PreHeat [°C] | REAL | Read | HoldingRegister | 1 | °C
6 | CoolVlv.Val | IO - Analog Output - Cooling [%] | REAL | Read | HoldingRegister | 2 | % | 0 - 100 %
4782 | Cool_Val_AO |  | UREAL16 |  | HoldingRegister | 2
9 | ExhAirFlow | IO - Probe - Air Flow - Return [m3/h] | REAL | Read | HoldingRegister | 3 | m3/h
10 | ExhAirP_Val | IO - Probe - Pressure - Return [Pa] | REAL | Read | HoldingRegister | 4 | Pa
11 | ExhTemp.Val | IO - Probe - Temperature - Recovery [°C] | REAL | Read | HoldingRegister | 5 | °C
12 | ExtTemp.Val | IO - Probe - Temperature - External [°C] | REAL | Read | HoldingRegister | 6 | °C
16 | HeatRecovery_Val | IO - Analog Output - Rotary - Value [%] | REAL | Read | HoldingRegister | 7 | % | 0 - 100 %
17 | HeatVlv.Val | IO - Analog Output - Heater [%] | REAL | Read | HoldingRegister | 8 | % | 0 - 100 %
4777 | Heat_Val_AO |  | UREAL16 |  | HoldingRegister | 8
19 | Hum_THTN_1 | IO - Probe - Humidity - TH Room [%] | REAL | Read | HoldingRegister | 9 | % | 0 - 100 %
22 | MB_Devices.MB_MainBoard_1.AI_Temp_Fan_Return | IO - Module IO - Temperature Fan Return [°C] | REAL | Read | HoldingRegister | 10 | °C
23 | MB_Devices.MB_MainBoard_1.AI_Temp_Fan_Supply | IO - Module IO - Temperature Fan Supply [°C] | REAL | Read | HoldingRegister | 11 | °C
24 | MB_Devices.MB_MainBoard_1.AO_01_Read | IO - Module IO - Analog output 1 [%] | REAL | Read | HoldingRegister | 12 | %
25 | MB_Devices.MB_MainBoard_1.AO_02_Read | IO - Module IO - Analog output 2 [%] | REAL | Read | HoldingRegister | 13 | %
26 | MB_Devices.MB_MainBoard_1.AO_03_Read | IO - Module IO - Analog output 3 [%] | REAL | Read | HoldingRegister | 14 | %
27 | MB_Devices.MB_MainBoard_1.AO_04_Read | IO - Module IO - Analog output 4 [%] | REAL | Read | HoldingRegister | 15 | %
28 | MB_Devices.MB_MainBoard_1.Humid_Return | IO - Module IO - Humidity Return [%] | REAL | Read | HoldingRegister | 16 | %
29 | MB_Devices.MB_MainBoard_1.Pressure_Fan_Return | IO - Module IO - Pressure Fan Return [Pa] | REAL | Read | HoldingRegister | 17 | Pa
30 | MB_Devices.MB_MainBoard_1.Pressure_Fan_Supply | IO - Module IO - Pressure Fan Supply [Pa] | REAL | Read | HoldingRegister | 18 | Pa
31 | MB_Devices.MB_MainBoard_1.Pressure_Filter_Return | IO - Module IO - Pressure Filter Return [Pa] | REAL | Read | HoldingRegister | 19 | Pa
32 | MB_Devices.MB_MainBoard_1.Pressure_Filter_Supply | IO - Module IO - Pressure Filter Supply [Pa] | REAL | Read | HoldingRegister | 20 | Pa
33 | MB_Devices.MB_MainBoard_1.Supply_24V_Read | IO - Module IO - Supply 24V [V] | REAL | Read | HoldingRegister | 21 | V
34 | MB_Devices.MB_MainBoard_1.Supply_Control_Read | IO - Module IO - Supply Controller [V] | REAL | Read | HoldingRegister | 22 | V
35 | MB_Devices.MB_MainBoard_1.Temp_Return | IO - Module IO - Temperature Return [°C] | REAL | Read | HoldingRegister | 23 | °C
36 | MixDampReq_Fresh | IO - Analog Output - Damper - External [%] | REAL | Read | HoldingRegister | 24 | % | 0 - 100 %
37 | ModulHum.Val | IO - Analog Output - Humidifier [%] | REAL | Read | HoldingRegister | 25 | % | 0 - 100 %
4769 | Humid_Val_AO |  | UREAL16 |  | HoldingRegister | 25
38 | ModulMixDamp_Val | IO - Analog Output - Damper - Mixing [%] | REAL | Read | HoldingRegister | 26 | % | 0 - 100 %
39 | ModulPreHeat.Val | IO - Analog Output - PreHeater [%] | REAL | Read | HoldingRegister | 27 | % | 0 - 100 %
4768 | PreHeat_Val_AO |  | UREAL16 |  | HoldingRegister | 27
42 | RecSupplyTemp.Val | IO - Probe - Temperature - Supply after recovery [°C] | REAL | Read | HoldingRegister | 28 | °C
44 | ReHeatVlv.Val | IO - Analog Output - ReHeater [%] | REAL | Read | HoldingRegister | 29 | % | 0 - 100 %
4767 | ReHeat_Val_AO |  | UREAL16 |  | HoldingRegister | 29
46 | RetAir_CO2_Val | IO - Probe - CO2 - Return [ppm] | REAL | Read | HoldingRegister | 30 | ppm
48 | RetHum_Val | IO - Probe - Humidity - Return [%] | REAL | Read | HoldingRegister | 31 | % | 0 - 100 %
49 | RetTemp.Val | IO - Probe - Temperature - Return / Room [°C] | REAL | Read | HoldingRegister | 32 | °C
51 | SupplyAirFlow | IO - Probe - Air Flow - Supply [m3/h] | REAL | Read | HoldingRegister | 33 | m3/h
52 | SupplyAirP_Val | IO - Probe - Pressure - Supply [Pa] | REAL | Read | HoldingRegister | 34 | Pa
54 | SupplyHum_Val | IO - Probe - Humidity - Supply [%] | REAL | Read | HoldingRegister | 35 | % | 0 - 100 %
55 | SupplyTemp.Val | IO - Probe - Temperature - Supply [°C] | REAL | Read | HoldingRegister | 36 | °C
56 | Temp_THTN_1 | IO - Probe - Temperature - TH Room [°C] | REAL | Read | HoldingRegister | 37 | °C
57 | W_HeatCoilTemp.Val | IO - Probe - Temperature - Water Heat [°C] | REAL | Read | HoldingRegister | 38 | °C
58 | W_PreHeatCoilTemp.Val | IO - Probe - Temperature - Water PreHeat [°C] | REAL | Read | HoldingRegister | 39 | °C
60 | Y1Out_HW | IO - Analog Output - Y1 [%] | REAL | Read | HoldingRegister | 40 | % | 0 - 100 %
61 | Y2Out_HW | IO - Analog Output - Y2 [%] | REAL | Read | HoldingRegister | 41 | % | 0 - 100 %
62 | Y3Out_HW | IO - Analog Output - Y3 [%] | REAL | Read | HoldingRegister | 42 | % | 0 - 100 %
64 | ExhFan_1.Current | MO - Fan - Return 1 - Current [A] | REAL | Read | HoldingRegister | 43 | A
65 | ExhFan_1.DriveTemp | MO - Fan - Return 1 - Drive temperature [°C] | REAL | Read | HoldingRegister | 44 | °C | USA
66 | ExhFan_1.Freq | MO - Fan - Return 1 - Frequence [Hz] | REAL | Read | HoldingRegister | 45 | Hz
67 | ExhFan_1.kWh | MO - Fan - Return 1 - Consumption [kWh] | REAL | Read | HoldingRegister | 46 | kWh | USA
68 | ExhFan_1.Power | MO - Fan - Return 1 - Power [W] | REAL | Read | HoldingRegister | 47 | W
69 | ExhFan_1.Rpm | MO - Fan - Return 1 - Speed [RPM] | REAL | Read | HoldingRegister | 48 | RPM
70 | ExhFan_1.Voltage | MO - Fan - Return 1 - Voltage [V] | REAL | Read | HoldingRegister | 49 | V
71 | ExhFan_10.Current | MO - Fan - Return 10 - Current [A] | REAL | Read | HoldingRegister | 50 | A
72 | ExhFan_10.DriveTemp | MO - Fan - Return 10 - Drive temperature [°C] | REAL | Read | HoldingRegister | 51 | °C | USA
73 | ExhFan_10.Freq | MO - Fan - Return 10 - Frequence [Hz] | REAL | Read | HoldingRegister | 52 | Hz
74 | ExhFan_10.kWh | MO - Fan - Return 10 - Consumption [kWh] | REAL | Read | HoldingRegister | 53 | kWh | USA
75 | ExhFan_10.Power | MO - Fan - Return 10 - Power [W] | REAL | Read | HoldingRegister | 54 | W
76 | ExhFan_10.Rpm | MO - Fan - Return 10 - Speed [RPM] | REAL | Read | HoldingRegister | 55 | RPM
77 | ExhFan_10.Voltage | MO - Fan - Return 10 - Voltage [V] | REAL | Read | HoldingRegister | 56 | V
78 | ExhFan_2.Current | MO - Fan - Return 2 - Current [A] | REAL | Read | HoldingRegister | 57 | A
79 | ExhFan_2.DriveTemp | MO - Fan - Return 2 - Drive temperature [°C] | REAL | Read | HoldingRegister | 58 | °C | USA
80 | ExhFan_2.Freq | MO - Fan - Return 2 - Frequence [Hz] | REAL | Read | HoldingRegister | 59 | Hz
81 | ExhFan_2.kWh | MO - Fan - Return 2 - Consumption [kWh] | REAL | Read | HoldingRegister | 60 | kWh | USA
82 | ExhFan_2.Power | MO - Fan - Return 2 - Power [W] | REAL | Read | HoldingRegister | 61 | W
83 | ExhFan_2.Rpm | MO - Fan - Return 2 - Speed [RPM] | REAL | Read | HoldingRegister | 62 | RPM
84 | ExhFan_2.Voltage | MO - Fan - Return 2 - Voltage [V] | REAL | Read | HoldingRegister | 63 | V
85 | ExhFan_3.Current | MO - Fan - Return 3 - Current [A] | REAL | Read | HoldingRegister | 64 | A
86 | ExhFan_3.DriveTemp | MO - Fan - Return 3 - Drive temperature [°C] | REAL | Read | HoldingRegister | 65 | °C | USA
87 | ExhFan_3.Freq | MO - Fan - Return 3 - Frequence [Hz] | REAL | Read | HoldingRegister | 66 | Hz
88 | ExhFan_3.kWh | MO - Fan - Return 3 - Consumption [kWh] | REAL | Read | HoldingRegister | 67 | kWh | USA
89 | ExhFan_3.Power | MO - Fan - Return 3 - Power [W] | REAL | Read | HoldingRegister | 68 | W
90 | ExhFan_3.Rpm | MO - Fan - Return 3 - Speed [RPM] | REAL | Read | HoldingRegister | 69 | RPM
91 | ExhFan_3.Voltage | MO - Fan - Return 3 - Voltage [V] | REAL | Read | HoldingRegister | 70 | V
92 | ExhFan_4.Current | MO - Fan - Return 4 - Current [A] | REAL | Read | HoldingRegister | 71 | A
93 | ExhFan_4.DriveTemp | MO - Fan - Return 4 - Drive temperature [°C] | REAL | Read | HoldingRegister | 72 | °C | USA
94 | ExhFan_4.Freq | MO - Fan - Return 4 - Frequence [Hz] | REAL | Read | HoldingRegister | 73 | Hz
95 | ExhFan_4.kWh | MO - Fan - Return 4 - Consumption [kWh] | REAL | Read | HoldingRegister | 74 | kWh | USA
96 | ExhFan_4.Power | MO - Fan - Return 4 - Power [W] | REAL | Read | HoldingRegister | 75 | W
97 | ExhFan_4.Rpm | MO - Fan - Return 4 - Speed [RPM] | REAL | Read | HoldingRegister | 76 | RPM
98 | ExhFan_4.Voltage | MO - Fan - Return 4 - Voltage [V] | REAL | Read | HoldingRegister | 77 | V
99 | ExhFan_5.Current | MO - Fan - Return 5 - Current [A] | REAL | Read | HoldingRegister | 78 | A
100 | ExhFan_5.DriveTemp | MO - Fan - Return 5 - Drive temperature [°C] | REAL | Read | HoldingRegister | 79 | °C | USA
101 | ExhFan_5.Freq | MO - Fan - Return 5 - Frequence [Hz] | REAL | Read | HoldingRegister | 80 | Hz
102 | ExhFan_5.kWh | MO - Fan - Return 5 - Consumption [kWh] | REAL | Read | HoldingRegister | 81 | kWh | USA
103 | ExhFan_5.Power | MO - Fan - Return 5 - Power [W] | REAL | Read | HoldingRegister | 82 | W
104 | ExhFan_5.Rpm | MO - Fan - Return 5 - Speed [RPM] | REAL | Read | HoldingRegister | 83 | RPM
105 | ExhFan_5.Voltage | MO - Fan - Return 5 - Voltage [V] | REAL | Read | HoldingRegister | 84 | V
106 | ExhFan_6.Current | MO - Fan - Return 6 - Current [A] | REAL | Read | HoldingRegister | 85 | A
107 | ExhFan_6.DriveTemp | MO - Fan - Return 6 - Drive temperature [°C] | REAL | Read | HoldingRegister | 86 | °C | USA
108 | ExhFan_6.Freq | MO - Fan - Return 6 - Frequence [Hz] | REAL | Read | HoldingRegister | 87 | Hz
109 | ExhFan_6.kWh | MO - Fan - Return 6 - Consumption [kWh] | REAL | Read | HoldingRegister | 88 | kWh | USA
110 | ExhFan_6.Power | MO - Fan - Return 6 - Power [W] | REAL | Read | HoldingRegister | 89 | W
111 | ExhFan_6.Rpm | MO - Fan - Return 6 - Speed [RPM] | REAL | Read | HoldingRegister | 90 | RPM
112 | ExhFan_6.Voltage | MO - Fan - Return 6 - Voltage [V] | REAL | Read | HoldingRegister | 91 | V
113 | ExhFan_7.Current | MO - Fan - Return 7 - Current [A] | REAL | Read | HoldingRegister | 92 | A
114 | ExhFan_7.DriveTemp | MO - Fan - Return 7 - Drive temperature [°C] | REAL | Read | HoldingRegister | 93 | °C | USA
115 | ExhFan_7.Freq | MO - Fan - Return 7 - Frequence [Hz] | REAL | Read | HoldingRegister | 94 | Hz
116 | ExhFan_7.kWh | MO - Fan - Return 7 - Consumption [kWh] | REAL | Read | HoldingRegister | 95 | kWh | USA
117 | ExhFan_7.Power | MO - Fan - Return 7 - Power [W] | REAL | Read | HoldingRegister | 96 | W
118 | ExhFan_7.Rpm | MO - Fan - Return 7 - Speed [RPM] | REAL | Read | HoldingRegister | 97 | RPM
119 | ExhFan_7.Voltage | MO - Fan - Return 7 - Voltage [V] | REAL | Read | HoldingRegister | 98 | V
120 | ExhFan_8.Current | MO - Fan - Return 8 - Current [A] | REAL | Read | HoldingRegister | 99 | A
121 | ExhFan_8.DriveTemp | MO - Fan - Return 8 - Drive temperature [°C] | REAL | Read | HoldingRegister | 100 | °C | USA
122 | ExhFan_8.Freq | MO - Fan - Return 8 - Frequence [Hz] | REAL | Read | HoldingRegister | 101 | Hz
123 | ExhFan_8.kWh | MO - Fan - Return 8 - Consumption [kWh] | REAL | Read | HoldingRegister | 102 | kWh | USA
124 | ExhFan_8.Power | MO - Fan - Return 8 - Power [W] | REAL | Read | HoldingRegister | 103 | W
125 | ExhFan_8.Rpm | MO - Fan - Return 8 - Speed [RPM] | REAL | Read | HoldingRegister | 104 | RPM
126 | ExhFan_8.Voltage | MO - Fan - Return 8 - Voltage [V] | REAL | Read | HoldingRegister | 105 | V
127 | ExhFan_9.Current | MO - Fan - Return 9 - Current [A] | REAL | Read | HoldingRegister | 106 | A
128 | ExhFan_9.DriveTemp | MO - Fan - Return 9 - Drive temperature [°C] | REAL | Read | HoldingRegister | 107 | °C | USA
129 | ExhFan_9.Freq | MO - Fan - Return 9 - Frequence [Hz] | REAL | Read | HoldingRegister | 108 | Hz
130 | ExhFan_9.kWh | MO - Fan - Return 9 - Consumption [kWh] | REAL | Read | HoldingRegister | 109 | kWh | USA
131 | ExhFan_9.Power | MO - Fan - Return 9 - Power [W] | REAL | Read | HoldingRegister | 110 | W
132 | ExhFan_9.Rpm | MO - Fan - Return 9 - Speed [RPM] | REAL | Read | HoldingRegister | 111 | RPM
133 | ExhFan_9.Voltage | MO - Fan - Return 9 - Voltage [V] | REAL | Read | HoldingRegister | 112 | V
134 | ExhFanVal | MO - Fan - Return - Value [%] | REAL | Read | HoldingRegister | 113 | % | 0 - 100 %
136 | Rotary.Current | MO - Recovery - Rotary - Current [A] | REAL | Read | HoldingRegister | 114 | A
137 | Rotary.DriveTemp | MO - Recovery - Rotary - Drive temperature [°C] | REAL | Read | HoldingRegister | 115 | °C | USA
138 | Rotary.Freq | MO - Recovery - Rotary - Frequence [Hz] | REAL | Read | HoldingRegister | 116 | Hz
139 | Rotary.kWh | MO - Recovery - Rotary - Consumption [kWh] | REAL | Read | HoldingRegister | 117 | kWh | USA
140 | Rotary.Power | MO - Recovery - Rotary - Power [W] | REAL | Read | HoldingRegister | 118 | W
141 | Rotary.Rpm | MO - Recovery - Rotary - Speed [RPM] | REAL | Read | HoldingRegister | 119 | RPM
142 | Rotary.Voltage | MO - Recovery - Rotary - Voltage [V] | REAL | Read | HoldingRegister | 120 | V
145 | SupplyFan_1.Current | MO - Fan - Supply 1 - Current [A] | REAL | Read | HoldingRegister | 121 | A
146 | SupplyFan_1.DriveTemp | MO - Fan - Supply 1 - Drive temperature [°C] | REAL | Read | HoldingRegister | 122 | °C | USA
147 | SupplyFan_1.Freq | MO - Fan - Supply 1 - Frequence [Hz] | REAL | Read | HoldingRegister | 123 | Hz
148 | SupplyFan_1.kWh | MO - Fan - Supply 1 - Consumption [kWh] | REAL | Read | HoldingRegister | 124 | kWh | USA
149 | SupplyFan_1.Power | MO - Fan - Supply 1 - Power [W] | REAL | Read | HoldingRegister | 125 | W
150 | SupplyFan_1.Rpm | MO - Fan - Supply 1 - Speed [RPM] | REAL | Read | HoldingRegister | 126 | RPM
151 | SupplyFan_1.Voltage | MO - Fan - Supply 1 - Voltage [V] | REAL | Read | HoldingRegister | 127 | V
152 | SupplyFan_10.Current | MO - Fan - Supply 10 - Current [A] | REAL | Read | HoldingRegister | 128 | A
153 | SupplyFan_10.DriveTemp | MO - Fan - Supply 10 - Drive temperature [°C] | REAL | Read | HoldingRegister | 129 | °C | USA
154 | SupplyFan_10.Freq | MO - Fan - Supply 10 - Frequence [Hz] | REAL | Read | HoldingRegister | 130 | Hz
155 | SupplyFan_10.kWh | MO - Fan - Supply 10 - Consumption [kWh] | REAL | Read | HoldingRegister | 131 | kWh | USA
156 | SupplyFan_10.Power | MO - Fan - Supply 10 - Power [W] | REAL | Read | HoldingRegister | 132 | W
157 | SupplyFan_10.Rpm | MO - Fan - Supply 10 - Speed [RPM] | REAL | Read | HoldingRegister | 133 | RPM
158 | SupplyFan_10.Voltage | MO - Fan - Supply 10 - Voltage [V] | REAL | Read | HoldingRegister | 134 | V
159 | SupplyFan_2.Current | MO - Fan - Supply 2 - Current [A] | REAL | Read | HoldingRegister | 135 | A
160 | SupplyFan_2.DriveTemp | MO - Fan - Supply 2 - Drive temperature [°C] | REAL | Read | HoldingRegister | 136 | °C | USA
161 | SupplyFan_2.Freq | MO - Fan - Supply 2 - Frequence [Hz] | REAL | Read | HoldingRegister | 137 | Hz
162 | SupplyFan_2.kWh | MO - Fan - Supply 2 - Consumption [kWh] | REAL | Read | HoldingRegister | 138 | kWh | USA
163 | SupplyFan_2.Power | MO - Fan - Supply 2 - Power [W] | REAL | Read | HoldingRegister | 139 | W
164 | SupplyFan_2.Rpm | MO - Fan - Supply 2 - Speed [RPM] | REAL | Read | HoldingRegister | 140 | RPM
165 | SupplyFan_2.Voltage | MO - Fan - Supply 2 - Voltage [V] | REAL | Read | HoldingRegister | 141 | V
166 | SupplyFan_3.Current | MO - Fan - Supply 3 - Current [A] | REAL | Read | HoldingRegister | 142 | A
167 | SupplyFan_3.DriveTemp | MO - Fan - Supply 3 - Drive temperature [°C] | REAL | Read | HoldingRegister | 143 | °C | USA
168 | SupplyFan_3.Freq | MO - Fan - Supply 3 - Frequence [Hz] | REAL | Read | HoldingRegister | 144 | Hz
169 | SupplyFan_3.kWh | MO - Fan - Supply 3 - Consumption [kWh] | REAL | Read | HoldingRegister | 145 | kWh | USA
170 | SupplyFan_3.Power | MO - Fan - Supply 3 - Power [W] | REAL | Read | HoldingRegister | 146 | W
171 | SupplyFan_3.Rpm | MO - Fan - Supply 3 - Speed [RPM] | REAL | Read | HoldingRegister | 147 | RPM
172 | SupplyFan_3.Voltage | MO - Fan - Supply 3 - Voltage [V] | REAL | Read | HoldingRegister | 148 | V
173 | SupplyFan_4.Current | MO - Fan - Supply 4 - Current [A] | REAL | Read | HoldingRegister | 149 | A
174 | SupplyFan_4.DriveTemp | MO - Fan - Supply 4 - Drive temperature [°C] | REAL | Read | HoldingRegister | 150 | °C | USA
175 | SupplyFan_4.Freq | MO - Fan - Supply 4 - Frequence [Hz] | REAL | Read | HoldingRegister | 151 | Hz
176 | SupplyFan_4.kWh | MO - Fan - Supply 4 - Consumption [kWh] | REAL | Read | HoldingRegister | 152 | kWh | USA
177 | SupplyFan_4.Power | MO - Fan - Supply 4 - Power [W] | REAL | Read | HoldingRegister | 153 | W
178 | SupplyFan_4.Rpm | MO - Fan - Supply 4 - Speed [RPM] | REAL | Read | HoldingRegister | 154 | RPM
179 | SupplyFan_4.Voltage | MO - Fan - Supply 4 - Voltage [V] | REAL | Read | HoldingRegister | 155 | V
180 | SupplyFan_5.Current | MO - Fan - Supply 5 - Current [A] | REAL | Read | HoldingRegister | 156 | A
181 | SupplyFan_5.DriveTemp | MO - Fan - Supply 5 - Drive temperature [°C] | REAL | Read | HoldingRegister | 157 | °C | USA
182 | SupplyFan_5.Freq | MO - Fan - Supply 5 - Frequence [Hz] | REAL | Read | HoldingRegister | 158 | Hz
183 | SupplyFan_5.kWh | MO - Fan - Supply 5 - Consumption [kWh] | REAL | Read | HoldingRegister | 159 | kWh | USA
184 | SupplyFan_5.Power | MO - Fan - Supply 5 - Power [W] | REAL | Read | HoldingRegister | 160 | W
185 | SupplyFan_5.Rpm | MO - Fan - Supply 5 - Speed [RPM] | REAL | Read | HoldingRegister | 161 | RPM
186 | SupplyFan_5.Voltage | MO - Fan - Supply 5 - Voltage [V] | REAL | Read | HoldingRegister | 162 | V
187 | SupplyFan_6.Current | MO - Fan - Supply 6 - Current [A] | REAL | Read | HoldingRegister | 163 | A
188 | SupplyFan_6.DriveTemp | MO - Fan - Supply 6 - Drive temperature [°C] | REAL | Read | HoldingRegister | 164 | °C | USA
189 | SupplyFan_6.Freq | MO - Fan - Supply 6 - Frequence [Hz] | REAL | Read | HoldingRegister | 165 | Hz
190 | SupplyFan_6.kWh | MO - Fan - Supply 6 - Consumption [kWh] | REAL | Read | HoldingRegister | 166 | kWh | USA
191 | SupplyFan_6.Power | MO - Fan - Supply 6 - Power [W] | REAL | Read | HoldingRegister | 167 | W
192 | SupplyFan_6.Rpm | MO - Fan - Supply 6 - Speed [RPM] | REAL | Read | HoldingRegister | 168 | RPM
193 | SupplyFan_6.Voltage | MO - Fan - Supply 6 - Voltage [V] | REAL | Read | HoldingRegister | 169 | V
194 | SupplyFan_7.Current | MO - Fan - Supply 7 - Current [A] | REAL | Read | HoldingRegister | 170 | A
195 | SupplyFan_7.DriveTemp | MO - Fan - Supply 7 - Drive temperature [°C] | REAL | Read | HoldingRegister | 171 | °C | USA
196 | SupplyFan_7.Freq | MO - Fan - Supply 7 - Frequence [Hz] | REAL | Read | HoldingRegister | 172 | Hz
197 | SupplyFan_7.kWh | MO - Fan - Supply 7 - Consumption [kWh] | REAL | Read | HoldingRegister | 173 | kWh | USA
198 | SupplyFan_7.Power | MO - Fan - Supply 7 - Power [W] | REAL | Read | HoldingRegister | 174 | W
199 | SupplyFan_7.Rpm | MO - Fan - Supply 7 - Speed [RPM] | REAL | Read | HoldingRegister | 175 | RPM
200 | SupplyFan_7.Voltage | MO - Fan - Supply 7 - Voltage [V] | REAL | Read | HoldingRegister | 176 | V
201 | SupplyFan_8.Current | MO - Fan - Supply 8 - Current [A] | REAL | Read | HoldingRegister | 177 | A
202 | SupplyFan_8.DriveTemp | MO - Fan - Supply 8 - Drive temperature [°C] | REAL | Read | HoldingRegister | 178 | °C | USA
203 | SupplyFan_8.Freq | MO - Fan - Supply 8 - Frequence [Hz] | REAL | Read | HoldingRegister | 179 | Hz
204 | SupplyFan_8.kWh | MO - Fan - Supply 8 - Consumption [kWh] | REAL | Read | HoldingRegister | 180 | kWh | USA
205 | SupplyFan_8.Power | MO - Fan - Supply 8 - Power [W] | REAL | Read | HoldingRegister | 181 | W
206 | SupplyFan_8.Rpm | MO - Fan - Supply 8 - Speed [RPM] | REAL | Read | HoldingRegister | 182 | RPM
207 | SupplyFan_8.Voltage | MO - Fan - Supply 8 - Voltage [V] | REAL | Read | HoldingRegister | 183 | V
208 | SupplyFan_9.Current | MO - Fan - Supply 9 - Current [A] | REAL | Read | HoldingRegister | 184 | A
209 | SupplyFan_9.DriveTemp | MO - Fan - Supply 9 - Drive temperature [°C] | REAL | Read | HoldingRegister | 185 | °C | USA
210 | SupplyFan_9.Freq | MO - Fan - Supply 9 - Frequence [Hz] | REAL | Read | HoldingRegister | 186 | Hz
211 | SupplyFan_9.kWh | MO - Fan - Supply 9 - Consumption [kWh] | REAL | Read | HoldingRegister | 187 | kWh | USA
212 | SupplyFan_9.Power | MO - Fan - Supply 9 - Power [W] | REAL | Read | HoldingRegister | 188 | W
213 | SupplyFan_9.Rpm | MO - Fan - Supply 9 - Speed [RPM] | REAL | Read | HoldingRegister | 189 | RPM
214 | SupplyFan_9.Voltage | MO - Fan - Supply 9 - Voltage [V] | REAL | Read | HoldingRegister | 190 | V
215 | SupplyFanVal | MO - Fan - Supply - Value [%] | REAL | Read | HoldingRegister | 191 | % | 0 - 100 %
218 | ExhFan_1_Power | MO - Fan - Return - Power [W] | REAL | Read | HoldingRegister | 192 | W
219 | SupplyFan_1_Power | MO - Fan - Supply - Power [W] | REAL | Read | HoldingRegister | 193 | W
220 | HC_Cool_1.Hrs | CT - Counter - Cooling - Device 1 [h] | UDINT | Read | HoldingRegister | 194 | h | 0 - 999999
221 | HC_Cool_2.Hrs | CT - Counter - Cooling - Device 2 [h] | UDINT | Read | HoldingRegister | 195 | h | 0 - 999999
222 | HC_ExhFan_1.Hrs | CT - Counter - Fan - Return 1 [h] | UDINT | Read | HoldingRegister | 196 | h | 0 - 999999
223 | HC_ExhFan_2.Hrs | CT - Counter - Fan - Return 2 [h] | UDINT | Read | HoldingRegister | 197 | h | 0 - 999999
224 | HC_Heat_1.Hrs | CT - Counter - Heating - Device 1 [h] | UDINT | Read | HoldingRegister | 198 | h | 0 - 999999
225 | HC_Heat_2.Hrs | CT - Counter - Heating - Device 2 [h] | UDINT | Read | HoldingRegister | 199 | h | 0 - 999999
226 | HC_Heat_Mod.Hrs | CT - Counter - Heating - Modulation [h] | UDINT | Read | HoldingRegister | 200 | h | 0 - 999999
227 | HC_Hum.Hrs | CT - Counter - Humidity [h] | UDINT | Read | HoldingRegister | 201 | h | 0 - 999999
228 | HC_PreHeat.Hrs | CT - Counter - PreHeating [h] | UDINT | Read | HoldingRegister | 202 | h | 0 - 999999
229 | HC_RecoveryPump.Hrs | CT - Counter - Recovery [h] | UDINT | Read | HoldingRegister | 203 | h | 0 - 999999
230 | HC_ReHeat.Hrs | CT - Counter - ReHeating [h] | UDINT | Read | HoldingRegister | 204 | h | 0 - 999999
231 | HC_SupplyFan_1.Hrs | CT - Counter - Fan - Supply 1 [h] | UDINT | Read | HoldingRegister | 205 | h | 0 - 999999
232 | HC_SupplyFan_2.Hrs | CT - Counter - Fan - Supply 2 [h] | UDINT | Read | HoldingRegister | 206 | h | 0 - 999999
233 | RegTemp | SP - Setpoint - Temperature - Current - Value [°C] | REAL | ReadWrite | HoldingRegister | 207 | °C
234 | SetTyp | SP - Work Mode | USINT | ReadWrite | HoldingRegister | 208 |  | 0 - OFF 1 - ECONOMY 2 - OPTIMAL 3 - COMFORT 4 - STANDBY 5 - AUTO
235 | UnitSetP.AirFlwSetP.Comfort | SP - Setpoint - Air Flow - Supply - 3 - Comfort [%] | REAL | ReadWrite | HoldingRegister | 209 | % | 0 - 100 %
236 | UnitSetP.AirFlwSetP.Economy | SP - Setpoint - Air Flow - Supply - 1 - Economy [%] | REAL | ReadWrite | HoldingRegister | 210 | % | 0 - 100 %
237 | UnitSetP.AirFlwSetP.PreComfort | SP - Setpoint - Air Flow - Supply - 2 - Optimal [%] | REAL | ReadWrite | HoldingRegister | 211 | % | 0 - 100 %
238 | UnitSetP.AirQualitySetP.Comfort | SP - Setpoint - Air Quality - 3 - Comfort [ppm] | REAL | ReadWrite | HoldingRegister | 212 | ppm
239 | UnitSetP.AirQualitySetP.Economy | SP - Setpoint - Air Quality - 1 - Economy [ppm] | REAL | ReadWrite | HoldingRegister | 213 | ppm
240 | UnitSetP.AirQualitySetP.PreComfort | SP - Setpoint - Air Quality - 2 - Optimal [ppm] | REAL | ReadWrite | HoldingRegister | 214 | ppm
241 | UnitSetP.HumSetP.Comfort | SP - Setpoint - Humidity - 3 - Comfort [%] | REAL | ReadWrite | HoldingRegister | 215 | % | 0 - 100 %
242 | UnitSetP.HumSetP.Economy | SP - Setpoint - Humidity - 1 - Economy [%] | REAL | ReadWrite | HoldingRegister | 216 | % | 0 - 100 %
243 | UnitSetP.HumSetP.PreComfort | SP - Setpoint - Humidity - 2 - Optimal [%] | REAL | ReadWrite | HoldingRegister | 217 | % | 0 - 100 %
244 | UnitSetP.RetAirFlwSetP.Comfort | SP - Setpoint - Air Flow - Return - 3 - Comfort [%] | REAL | ReadWrite | HoldingRegister | 218 | % | 0 - 100 %
245 | UnitSetP.RetAirFlwSetP.Economy | SP - Setpoint - Air Flow - Return - 1 - Economy [%] | REAL | ReadWrite | HoldingRegister | 219 | % | 0 - 100 %
246 | UnitSetP.RetAirFlwSetP.PreComfort | SP - Setpoint - Air Flow - Return - 2 - Optimal [%] | REAL | ReadWrite | HoldingRegister | 220 | % | 0 - 100 %
247 | UnitSetP.RoomTempSetP.Comfort | SP - Setpoint - Temperature - Room - 3 - Comfort [°C] | REAL | ReadWrite | HoldingRegister | 221 | °C
248 | UnitSetP.RoomTempSetP.Economy | SP - Setpoint - Temperature - Room - 1 - Economy [°C] | REAL | ReadWrite | HoldingRegister | 222 | °C
249 | UnitSetP.RoomTempSetP.PreComfort | SP - Setpoint - Temperature - Room - 2 - Optimal [°C] | REAL | ReadWrite | HoldingRegister | 223 | °C
250 | ActualSet | SP - Setpoint - Temperature - Actual [°C] | REAL | Read | HoldingRegister | 224 | °C
251 | CurrAirFlwSetP_Val | SP - Setpoint - Air Flow - Supply - Current - Value [%] | REAL | Read | HoldingRegister | 225 | % | 0 - 100 %
252 | CurrAirQualitySetP_Val | SP - Setpoint - Air Quality - Current - Value [ppm] | REAL | Read | HoldingRegister | 226 | ppm
253 | CurrHumSetP_Val | SP - Setpoint - Humidity - Current - Value [%] | REAL | Read | HoldingRegister | 227 | % | 0 - 100 %
254 | CurrRetAirFlwSetP_Val | SP - Setpoint - Air Flow - Return - Current - Value [%] | REAL | Read | HoldingRegister | 228 | % | 0 - 100 %
255 | CurrRoomTempSetP_Val | SP - Setpoint - Temperature - Room - Current - Value [°C] | REAL | Read | HoldingRegister | 229 | °C
256 | UnitSetP_AirFlwSetP_Comfort | SP - Setpoint - Air Flow - Supply - 3 - Comfort (Actual) [%] | REAL | Read | HoldingRegister | 230 | % | 0 - 100 %
257 | UnitSetP_AirFlwSetP_Comfort_2 | SP - Setpoint - Air Flow - Return - 3 - Comfort (Actual) [%] | REAL | Read | HoldingRegister | 231 | % | 0 - 100 %
258 | UnitSetP_AirFlwSetP_Economy | SP - Setpoint - Air Flow - Supply - 1 - Economy (Actual [%] | REAL | Read | HoldingRegister | 232 | % | 0 - 100 %
259 | UnitSetP_AirFlwSetP_Economy_2 | SP - Setpoint - Air Flow - Return - 1 - Economy (Actual [%] | REAL | Read | HoldingRegister | 233 | % | 0 - 100 %
260 | UnitSetP_AirFlwSetP_PreComfort | SP - Setpoint - Air Flow - Supply - 2 - Optimal (Actual [%] | REAL | Read | HoldingRegister | 234 | % | 0 - 100 %
261 | UnitSetP_AirFlwSetP_PreComfort_2 | SP - Setpoint - Air Flow - Return - 2 - Optimal (Actual [%] | REAL | Read | HoldingRegister | 235 | % | 0 - 100 %
262 | RecHeat_PowerTemp_T_kWh | ECO - Power Cool [kW] | REAL | Read | HoldingRegister | 236 | kW
263 | RecCool_PowerTemp_T_kWh | ECO - Power Cool [kWh] | REAL | Read | HoldingRegister | 237 | kWh
264 | Heat_PowerTemp_T_kWh | ECO - Power Cost - Constant [kWh] | REAL | Read | HoldingRegister | 238 | kWh
265 | Cool_PowerTemp_T_kWh | ECO - Power Cost - Constant - Mode ECO [kWh] | REAL | Read | HoldingRegister | 239 | kWh
266 | PowerElect_T_kWh_ECO | ECO - Power Cost - Constant - Mode Optimal [kWh] | REAL | Read | HoldingRegister | 240 | kWh
267 | PowerElect_T_kWh_Optimal | ECO - Power Cost - Constant - Mode Comfort [kWh] | REAL | Read | HoldingRegister | 241 | kWh
268 | PowerElect_T_kWh_Comfort | ECO - Power Cost [kWh] | REAL | Read | HoldingRegister | 242 | kWh
269 | SupplyFan_Power_E1 | ECO - Power Cost - Mode ECO [kWh] | REAL | Read | HoldingRegister | 243 | kWh
270 | ReturnFan_Power_E1 | ECO - Power Cost - Mode Optimal [kWh] | REAL | Read | HoldingRegister | 244 | kWh
271 | HC_Mode_ECO | ECO - Power Cost - Mode Comfort [kWh] | UDINT | Read | HoldingRegister | 245 | kWh
272 | HC_Mode_Comfort | ECO - Power Heat [kW] | UDINT | Read | HoldingRegister | 246 | kW
273 | HC_Mode_Optimal | ECO - Power Heat kWh [kWh] | UDINT | Read | HoldingRegister | 247 | kWh
274 | RecHeat_PowerTemp | ECO [kWh] | REAL | Read | HoldingRegister | 248 | kWh
275 | RecCool_PowerTemp | ECO [kWh] | REAL | Read | HoldingRegister | 249 | kWh
276 | Heat_PowerTemp | ECO [kWh] | REAL | Read | HoldingRegister | 250 | kWh
277 | Cool_PowerTemp | ECO [kWh] | REAL | Read | HoldingRegister | 251 | kWh
278 | RecHeat_PowerTemp_kWh | ECO [kWh] | REAL | Read | HoldingRegister | 252 | kWh
279 | RecCool_PowerTemp_kWh | ECO [kW] | REAL | Read | HoldingRegister | 253 | kW
280 | Heat_PowerTemp_kWh | ECO [kWh] | REAL | Read | HoldingRegister | 254 | kWh
281 | Cool_PowerTemp_kWh | ECO [kW] | REAL | Read | HoldingRegister | 255 | kW
282 | Recovery_Efficency | ECO [kWh] | REAL | Read | HoldingRegister | 256 | kWh
284 | Scheduler_OnOffUnit.Scheduler_1.CopyTo_Day | SCH - Scheduller - Time Band - Copy to Day | DINT | ReadWrite | HoldingRegister | 257 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN 7 - ALL
285 | Scheduler_OnOffUnit.Scheduler_1.Day | SCH - Scheduller - Time Band - Day | DINT | ReadWrite | HoldingRegister | 258 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN
4766 | Scheduler_OnOffUnit.Scheduler_1.VacationsDailyChk.CurrentWkDay |  | UInt |  | HoldingRegister | 258
288 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Hours | SCH - Scheduller - Monday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 259 | h | 00-23
289 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Mins | SCH - Scheduller - Monday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 260 | min. | 0 - 59
290 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].UnitStatus | SCH - Scheduller - Monday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 261 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
293 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Hours | SCH - Scheduller - Monday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 262 | h | 0 - 23
294 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Mins | SCH - Scheduller - Monday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 263 | min. | 0 - 59
295 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].UnitStatus | SCH - Scheduller - Monday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 264 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
298 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Hours | SCH - Scheduller - Monday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 265 | h | 0 - 23
299 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Mins | SCH - Scheduller - Monday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 266 | min. | 0 - 59
300 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].UnitStatus | SCH - Scheduller - Monday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 267 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
303 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Hours | SCH - Scheduller - Monday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 268 | h | 0 - 23
304 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Mins | SCH - Scheduller - Monday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 269 | min. | 0 - 59
305 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].UnitStatus | SCH - Scheduller - Monday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 270 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
308 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Hours | SCH - Scheduller - Tuesday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 271 | h | 0 - 23
309 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Mins | SCH - Scheduller - Tuesday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 272 | min. | 0 - 59
310 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].UnitStatus | SCH - Scheduller - Tuesday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 273 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
313 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Hours | SCH - Scheduller - Tuesday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 274 | h | 0 - 23
314 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Mins | SCH - Scheduller - Tuesday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 275 | min. | 0 - 59
315 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].UnitStatus | SCH - Scheduller - Tuesday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 276 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
318 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Hours | SCH - Scheduller - Tuesday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 277 | h | 0 - 23
319 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Mins | SCH - Scheduller - Tuesday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 278 | min. | 0 - 59
320 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].UnitStatus | SCH - Scheduller - Tuesday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 279 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
323 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Hours | SCH - Scheduller - Tuesday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 280 | h | 0 - 23
324 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Mins | SCH - Scheduller - Tuesday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 281 | min. | 0 - 59
325 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].UnitStatus | SCH - Scheduller - Tuesday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 282 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
328 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Hours | SCH - Scheduller - Wednesday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 283 | h | 0 - 23
329 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Mins | SCH - Scheduller - Wednesday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 284 | min. | 0 - 59
330 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].UnitStatus | SCH - Scheduller - Wednesday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 285 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
333 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Hours | SCH - Scheduller - Wednesday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 286 | h | 0 - 23
334 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Mins | SCH - Scheduller - Wednesday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 287 | min. | 0 - 59
335 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].UnitStatus | SCH - Scheduller - Wednesday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 288 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
338 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Hours | SCH - Scheduller - Wednesday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 289 | h | 0 - 23
339 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Mins | SCH - Scheduller - Wednesday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 290 | min. | 0 - 59
340 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].UnitStatus | SCH - Scheduller - Wednesday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 291 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
343 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Hours | SCH - Scheduller - Wednesday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 292 | h | 0 - 23
344 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Mins | SCH - Scheduller - Wednesday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 293 | min. | 0 - 59
345 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].UnitStatus | SCH - Scheduller - Wednesday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 294 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
348 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Hours | SCH - Scheduller - Thursday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 295 | h | 0 - 23
349 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Mins | SCH - Scheduller - Thursday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 296 | min. | 0 - 59
350 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].UnitStatus | SCH - Scheduller - Thursday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 297 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
353 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Hours | SCH - Scheduller - Thursday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 298 | h | 0 - 23
354 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Mins | SCH - Scheduller - Thursday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 299 | min. | 0 - 59
355 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].UnitStatus | SCH - Scheduller - Thursday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 300 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
358 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Hours | SCH - Scheduller - Thursday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 301 | h | 0 - 23
359 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Mins | SCH - Scheduller - Thursday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 302 | min. | 0 - 59
360 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].UnitStatus | SCH - Scheduller - Thursday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 303 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
363 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Hours | SCH - Scheduller - Thursday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 304 | h | 0 - 23
364 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Mins | SCH - Scheduller - Thursday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 305 | min. | 0 - 59
365 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].UnitStatus | SCH - Scheduller - Thursday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 306 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
368 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Hours | SCH - Scheduller - Friday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 307 | h | 0 - 23
369 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Mins | SCH - Scheduller - Friday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 308 | min. | 0 - 59
370 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].UnitStatus | SCH - Scheduller - Friday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 309 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
373 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Hours | SCH - Scheduller - Friday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 310 | h | 0 - 23
374 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Mins | SCH - Scheduller - Friday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 311 | min. | 0 - 59
375 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].UnitStatus | SCH - Scheduller - Friday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 312 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
378 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Hours | SCH - Scheduller - Friday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 313 | h | 0 - 23
379 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Mins | SCH - Scheduller - Friday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 314 | min. | 0 - 59
380 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].UnitStatus | SCH - Scheduller - Friday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 315 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
383 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Hours | SCH - Scheduller - Friday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 316 | h | 0 - 23
384 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Mins | SCH - Scheduller - Friday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 317 | min. | 0 - 59
385 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].UnitStatus | SCH - Scheduller - Friday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 318 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
388 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Hours | SCH - Scheduller - Saturday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 319 | h | 0 - 23
389 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Mins | SCH - Scheduller - Saturday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 320 | min. | 0 - 59
390 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].UnitStatus | SCH - Scheduller - Saturday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 321 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
393 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Hours | SCH - Scheduller - Saturday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 322 | h | 0 - 23
394 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Mins | SCH - Scheduller - Saturday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 323 | min. | 0 - 59
395 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].UnitStatus | SCH - Scheduller - Saturday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 324 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
398 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Hours | SCH - Scheduller - Saturday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 325 | h | 0 - 23
399 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Mins | SCH - Scheduller - Saturday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 326 | min. | 0 - 59
400 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].UnitStatus | SCH - Scheduller - Saturday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 327 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
403 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Hours | SCH - Scheduller - Saturday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 328 | h | 0 - 23
404 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Mins | SCH - Scheduller - Saturday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 329 | min. | 0 - 59
405 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].UnitStatus | SCH - Scheduller - Saturday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 330 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
408 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Hours | SCH - Scheduller - Sunday - 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 331 | h | 0 - 23
409 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Mins | SCH - Scheduller - Sunday - 1 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 332 | min. | 0 - 59
410 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].UnitStatus | SCH - Scheduller - Sunday - 1 - UnitStatus | USINT | ReadWrite | HoldingRegister | 333 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
413 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Hours | SCH - Scheduller - Sunday - 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 334 | h | 0 - 23
414 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Mins | SCH - Scheduller - Sunday - 2 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 335 | min. | 0 - 59
415 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].UnitStatus | SCH - Scheduller - Sunday - 2 - UnitStatus | USINT | ReadWrite | HoldingRegister | 336 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
418 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Hours | SCH - Scheduller - Sunday - 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 337 | h | 0 - 23
419 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Mins | SCH - Scheduller - Sunday - 3 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 338 | min. | 0 - 59
420 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].UnitStatus | SCH - Scheduller - Sunday - 3 - UnitStatus | USINT | ReadWrite | HoldingRegister | 339 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
423 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Hours | SCH - Scheduller - Sunday - 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 340 | h | 0 - 23
424 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Mins | SCH - Scheduller - Sunday - 4 - Mins [min.] | USINT | ReadWrite | HoldingRegister | 341 | min. | 0 - 59
425 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].UnitStatus | SCH - Scheduller - Sunday - 4 - UnitStatus | USINT | ReadWrite | HoldingRegister | 342 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
426 | Scheduler_OnOffUnit.Scheduler_1.EnDayCopy | SCH - Scheduller - Time Band - Enable Copy to Day | USINT | ReadWrite | HoldingRegister | 343 |  | 0 - NO 1 - YES
427 | Scheduler_OnOffUnit.Scheduler_1.SaveData | SCH - Scheduller - Time Band - Save Data | USINT | ReadWrite | HoldingRegister | 344 |  | 0 - NO 1 - YES
429 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].SpecialDay | SCH - Scheduller - Special Days 1 - Day | USINT | ReadWrite | HoldingRegister | 345 |  | 1 - 31
430 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].SpecialMonth | SCH - Scheduller - Special Days 1 - Month | USINT | ReadWrite | HoldingRegister | 346 |  | 1 - 12
431 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].UnitStatus | SCH - Scheduller - Special Days 1 - Unit Status | USINT | ReadWrite | HoldingRegister | 347 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
433 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].SpecialDay | SCH - Scheduller - Special Days 2 - Day | USINT | ReadWrite | HoldingRegister | 348 |  | 1 - 31
434 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].SpecialMonth | SCH - Scheduller - Special Days 2 - Month | USINT | ReadWrite | HoldingRegister | 349 |  | 1 - 12
435 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].UnitStatus | SCH - Scheduller - Special Days 2 - Unit Status | USINT | ReadWrite | HoldingRegister | 350 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
437 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].SpecialDay | SCH - Scheduller - Special Days 3 - Day | USINT | ReadWrite | HoldingRegister | 351 |  | 1 - 31
438 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].SpecialMonth | SCH - Scheduller - Special Days 3 - Month | USINT | ReadWrite | HoldingRegister | 352 |  | 1 - 12
439 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].UnitStatus | SCH - Scheduller - Special Days 3 - Unit Status | USINT | ReadWrite | HoldingRegister | 353 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
441 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].SpecialDay | SCH - Scheduller - Special Days 4 - Day | USINT | ReadWrite | HoldingRegister | 354 |  | 1 - 31
442 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].SpecialMonth | SCH - Scheduller - Special Days 4 - Month | USINT | ReadWrite | HoldingRegister | 355 |  | 1 - 12
443 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].UnitStatus | SCH - Scheduller - Special Days 4 - Unit Status | USINT | ReadWrite | HoldingRegister | 356 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
445 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].SpecialDay | SCH - Scheduller - Special Days 5 - Day | USINT | ReadWrite | HoldingRegister | 357 |  | 1 - 31
446 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].SpecialMonth | SCH - Scheduller - Special Days 5 - Month | USINT | ReadWrite | HoldingRegister | 358 |  | 1 - 12
447 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].UnitStatus | SCH - Scheduller - Special Days 5 - Unit Status | USINT | ReadWrite | HoldingRegister | 359 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
449 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].SpecialDay | SCH - Scheduller - Special Days 6 - Day | USINT | ReadWrite | HoldingRegister | 360 |  | 1 - 31
450 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].SpecialMonth | SCH - Scheduller - Special Days 6 - Month | USINT | ReadWrite | HoldingRegister | 361 |  | 1 - 12
451 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].UnitStatus | SCH - Scheduller - Special Days 6 - Unit Status | USINT | ReadWrite | HoldingRegister | 362 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
453 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Hours | SCH - Scheduller - Time Band 1 - Hours [h] | USINT | ReadWrite | HoldingRegister | 363 | h | 0 - 23
454 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Mins | SCH - Scheduller - Time Band 1 - Minute [min.] | USINT | ReadWrite | HoldingRegister | 364 | min. | 0 - 59
455 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].UnitStatus | SCH - Scheduller - Time Band 1 - Unit Status | USINT | ReadWrite | HoldingRegister | 365 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
457 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Hours | SCH - Scheduller - Time Band 2 - Hours [h] | USINT | ReadWrite | HoldingRegister | 366 | h | 0 - 23
458 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Mins | SCH - Scheduller - Time Band 2 - Minute [min.] | USINT | ReadWrite | HoldingRegister | 367 | min. | 0 - 59
459 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].UnitStatus | SCH - Scheduller - Time Band 2 - Unit Status | USINT | ReadWrite | HoldingRegister | 368 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
461 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Hours | SCH - Scheduller - Time Band 3 - Hours [h] | USINT | ReadWrite | HoldingRegister | 369 | h | 0 - 23
462 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Mins | SCH - Scheduller - Time Band 3 - Minute [min.] | USINT | ReadWrite | HoldingRegister | 370 | min. | 0 - 59
463 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].UnitStatus | SCH - Scheduller - Time Band 3 - Unit Status | USINT | ReadWrite | HoldingRegister | 371 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
465 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Hours | SCH - Scheduller - Time Band 4 - Hours [h] | USINT | ReadWrite | HoldingRegister | 372 | h | 0 - 23
466 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Mins | SCH - Scheduller - Time Band 4 - Minute [min.] | USINT | ReadWrite | HoldingRegister | 373 | min. | 0 - 59
467 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].UnitStatus | SCH - Scheduller - Time Band 4 - Unit Status | USINT | ReadWrite | HoldingRegister | 374 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
469 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].EndDay | SCH - Scheduller - Periods 1 - End Day | USINT | ReadWrite | HoldingRegister | 375 |  | 1 - 31
470 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].EndMonth | SCH - Scheduller - Periods 1 - End Month | USINT | ReadWrite | HoldingRegister | 376 |  | 1 - 12
471 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].StartDay | SCH - Scheduller - Periods 1 - Start Day | USINT | ReadWrite | HoldingRegister | 377 |  | 1 - 31
472 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].StartMonth | SCH - Scheduller - Periods 1 - Start Month | USINT | ReadWrite | HoldingRegister | 378 |  | 1 - 12
473 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].UnitStatus | SCH - Scheduller - Periods 1 - Unit Status | USINT | ReadWrite | HoldingRegister | 379 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
475 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].EndDay | SCH - Scheduller - Periods 2 - End Day | USINT | ReadWrite | HoldingRegister | 380 |  | 1 - 31
476 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].EndMonth | SCH - Scheduller - Periods 2 - End Month | USINT | ReadWrite | HoldingRegister | 381 |  | 1 - 12
477 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].StartDay | SCH - Scheduller - Periods 2 - Start Day | USINT | ReadWrite | HoldingRegister | 382 |  | 1 - 31
478 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].StartMonth | SCH - Scheduller - Periods 2 - Start Month | USINT | ReadWrite | HoldingRegister | 383 |  | 1 - 12
479 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].UnitStatus | SCH - Scheduller - Periods 2 - Unit Status | USINT | ReadWrite | HoldingRegister | 384 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
481 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].EndDay | SCH - Scheduller - Periods 3 - End Day | USINT | ReadWrite | HoldingRegister | 385 |  | 1 - 31
482 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].EndMonth | SCH - Scheduller - Periods 3 - End Month | USINT | ReadWrite | HoldingRegister | 386 |  | 1 - 12
483 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].StartDay | SCH - Scheduller - Periods 3 - Start Day | USINT | ReadWrite | HoldingRegister | 387 |  | 1 - 31
484 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].StartMonth | SCH - Scheduller - Periods 3 - Start Month | USINT | ReadWrite | HoldingRegister | 388 |  | 1 - 12
485 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].UnitStatus | SCH - Scheduller - Periods 3 - Unit Status | USINT | ReadWrite | HoldingRegister | 389 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
486 | SetTypSched | SP - WorkMode - Actual | USINT | Read | HoldingRegister | 390
487 | TypScheduler | SCH - Scheduller - Type | USINT | ReadWrite | HoldingRegister | 391 |  | 0 - NONE 1 - BOARD 2 - HMI
489 | CurrUnitStatus | SCH - Scheduller - Actual mode from scheduller | USINT | Read | HoldingRegister | 392 |  | 0 - OFF 1 - ECO 2 - Optimal 3 - Comfort
2004 | DayIn | CLK - Time - Setting - Day | UINT | ReadWrite | HoldingRegister | 393 |  | 1 - 31
2006 | GeneralMng.Zone_TZ | CLK - Time - Setting - Zone | UDINT | ReadWrite | HoldingRegister | 394
2007 | HourIn | CLK - Time - Setting - Hour [h] | UINT | ReadWrite | HoldingRegister | 395 | h
2008 | MinuteIn | CLK - Time - Setting - Minute [min.] | UINT | ReadWrite | HoldingRegister | 396 | min.
2009 | MonthIn | CLK - Time - Setting - Month | UINT | ReadWrite | HoldingRegister | 397 |  | 1 - 12
2010 | SecondIn | CLK - Time - Setting - Second [sec.] | UINT | ReadWrite | HoldingRegister | 398 | sec.
2011 | YearIn | CLK - Time - Setting - Year | UINT | ReadWrite | HoldingRegister | 399 |  | 0 - 99
2012 | Day | CLK - Time - Day | UINT | Read | HoldingRegister | 400 |  | 1 - 31
2013 | DayOfWeek | CLK - Time - Setting - Day of Week | UINT | Read | HoldingRegister | 401 |  | 1 - MON 2 - TUE 3 - WED 4 - THU 5 - FRI 6 - SAT 7 - SUN
2014 | Hour | CLK - Time - Hour [h] | UINT | Read | HoldingRegister | 402 | h
2015 | Minute | CLK - Time - Minute [min.] | UINT | Read | HoldingRegister | 403 | min.
2016 | Month | CLK - Time - Month | UINT | Read | HoldingRegister | 404 |  | 1 - 12
2017 | Second | CLK - Time - Second [sec.] | UINT | Read | HoldingRegister | 405 | sec.
2018 | Year | CLK - Time - Year | UINT | Read | HoldingRegister | 406 |  | 0 - 99
2019 | AlrmExhAirP_Msk | PAR - Fan - Return - Warning Threshold Air Pressure [Pa] | REAL | ReadWrite | HoldingRegister | 407 | Pa
2020 | AlrmSupplyAirP_Msk | PAR - Fan - Supply - Warning Threshold Air Pressure [Pa] | REAL | ReadWrite | HoldingRegister | 408 | Pa
2021 | AFreezeExtMaxTemp | PAR - Heating - Antifreeze - External Temperature - Maximum [°C] | REAL | ReadWrite | HoldingRegister | 409 | °C
2022 | AFreezeExtMinTemp | PAR - Heating - Antifreeze - External Temperature - Minimum [°C] | REAL | ReadWrite | HoldingRegister | 410 | °C
2023 | AfreezeHeatMax | PAR - Heating - Antifreeze - Valve Open - Maximum [%] | REAL | ReadWrite | HoldingRegister | 411 | % | 0 - 100 %
2024 | AFreezeHeatMaxT | PAR - Heating - Antifreeze - Time - Maximum [sec.] | UINT | ReadWrite | HoldingRegister | 412 | sec.
2025 | AfreezeHeatMin | PAR - Heating - Antifreeze - Valve Open - Minimum [%] | REAL | ReadWrite | HoldingRegister | 413 | % | 0 - 100 %
2026 | AFreezeHeatMinT | PAR - Heating - Antifreeze - Time - Minimum [sec.] | UINT | ReadWrite | HoldingRegister | 414 | sec.
2027 | AlrmExhAirP | PAR - Fan - Return - Warning Threshold Pressure [Pa] | REAL | ReadWrite | HoldingRegister | 415 | Pa
2028 | AlrmSupplyAirP | PAR - Fan - Supply - Warning Threshold Pressure [Pa] | REAL | ReadWrite | HoldingRegister | 416 | Pa
2030 | Cool_1.Man | PAR - Cooling - Main Cooler - Manual Digital | USINT | ReadWrite | HoldingRegister | 417 |  | 0 - AUTO 1 - OFF 2 - ON
2032 | Cool_2.Man | PAR - Cooling - Main Cooler DX - Manual Digital | USINT | ReadWrite | HoldingRegister | 418 |  | 0 - AUTO 1 - OFF 2 - ON
2033 | CoolDX_ResTyp | PAR - Cooling - Main Cooler DX - Operating Block | USINT | ReadWrite | HoldingRegister | 419 |  | 0 - NONE 1 - ECO 2 - ECO + OPTIMAL
2034 | CoolExtTempThrsh | PAR - Regulation - ChangeOver - External Temperature - Cool Threshold [°C] | REAL | ReadWrite | HoldingRegister | 420 | °C
2035 | CoolMinOffT | PAR - Cooling - Main Cooler DX - Time - Minimum OFF [sec.] | UINT | ReadWrite | HoldingRegister | 421 | sec.
2036 | CoolMinOnOnSameT | PAR - Cooling - Main Cooler DX - Time - Between starts [sec.] | UINT | ReadWrite | HoldingRegister | 422 | sec.
2037 | CoolMinOnT | PAR - Cooling - Main Cooler DX - Time - Minimum ON [sec.] | UINT | ReadWrite | HoldingRegister | 423 | sec.
2038 | CoolVlv.Man | PAR - Cooling - Main Cooler - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 424 | % | 0 - 100 %
2039 | DeltaDew_PID.Kp | PAR - Regulation PID - Humidity - Dewpoint - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 425 | Kp
2040 | DeltaDew_PID.Ti | PAR - Regulation PID - Humidity - Dewpoint - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 426 | Ti - sec.
2041 | DeltaDewTemp | PAR - Regulation PID - Humidity - Dewpoint - Delta [%] | REAL | ReadWrite | HoldingRegister | 427 | % | 0 - 100 %
2042 | DevCfg_PID_Seq_CO2[0].Kp | PAR - Regulation PID - CO2 Mixing - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 428 | Kp
2043 | DevCfg_PID_Seq_CO2[0].Ti | PAR - Regulation PID - CO2 Mixing - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 429 | Ti - sec.
2044 | DevCfg_PID_Seq_CO2[1].Kp | PAR - Regulation PID - CO2 Fan Compensation - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 430 | Kp
2045 | DevCfg_PID_Seq_CO2[1].Ti | PAR - Regulation PID - CO2 Fan Compensation - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 431 | Ti - sec.
2046 | DevCfg_PID_Seq_Cool[2].Kp | PAR - Regulation PID - Recovery - Cooling - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 432 | Kp
2047 | DevCfg_PID_Seq_Cool[2].Ti | PAR - Regulation PID - Recovery - Cooling - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 433 | Ti - sec.
2048 | DevCfg_PID_Seq_Cool[4].Kp | PAR - Regulation PID - Main Cooler - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 434 | Kp
2049 | DevCfg_PID_Seq_Cool[4].Ti | PAR - Regulation PID - Main Cooler - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 435 | Ti - sec.
2050 | DevCfg_PID_Seq_Cool[5].Kp | PAR - Regulation PID - Mixing - Cooling - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 436 | Kp
2051 | DevCfg_PID_Seq_Cool[5].Ti | PAR - Regulation PID - Mixing - Cooling - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 437 | Ti - sec.
2052 | DevCfg_PID_Seq_Heat[2].Kp | PAR - Regulation PID - Recovery - Heating - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 438 | Kp
2053 | DevCfg_PID_Seq_Heat[2].Ti | PAR - Regulation PID - Recovery - Heating - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 439 | Ti - sec.
2054 | DevCfg_PID_Seq_Heat[4].Kp | PAR - Regulation PID - Main Heater - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 440 | Kp
2055 | DevCfg_PID_Seq_Heat[4].Ti | PAR - Regulation PID - Main Heater - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 441 | Ti - sec.
2056 | DevCfg_PID_Seq_Heat[5].Kp | PAR - Regulation PID - Mixing - Heating - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 442 | Kp
2057 | DevCfg_PID_Seq_Heat[5].Ti | PAR - Regulation PID - Mixing - Heating - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 443 | Ti - sec.
2058 | DevCfg_PID_Seq_Heat[6].Kp | PAR - Regulation PID - ReHeating - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 444 | Kp
2059 | DevCfg_PID_Seq_Heat[6].Ti | PAR - Regulation PID - ReHeating - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 445 | Ti - sec.
2060 | DOff_ExhFan | PAR - Fan - Return - Time - OFF Delay [sec.] | UINT | ReadWrite | HoldingRegister | 446 | sec.
2061 | DOff_SupplyFan | PAR - Fan - Supply - Time - OFF Delay [sec.] | UINT | ReadWrite | HoldingRegister | 447 | sec.
2062 | DT_ChangeHum | PAR - Humidity - Time - Change Delay [sec.] | UDINT | ReadWrite | HoldingRegister | 448 | sec.
2063 | DT_Dmp | PAR - Fan - Supply - Time - OFF Damper [sec.] | UINT | ReadWrite | HoldingRegister | 449 | sec.
2064 | DT_ExhFan | PAR - Fan - Return - Time - ON Delay [sec.] | UINT | ReadWrite | HoldingRegister | 450 | sec.
2065 | DT_SupplyFan | PAR - Fan - Supply - Time - ON Delay [sec.] | UINT | ReadWrite | HoldingRegister | 451 | sec.
2070 | ExhAirFlowSet_Msk | PAR - Fan - Return - Flow - Maximum [m3/h] | REAL | ReadWrite | HoldingRegister | 452 | m3/h
2071 | ExhAirPSet_Msk | PAR - Fan - Return - Pressure - Maximum [Pa] | REAL | ReadWrite | HoldingRegister | 453 | Pa
2072 | FastCoolThrsh | PAR - Recovery - Cooling Limit [%] | REAL | ReadWrite | HoldingRegister | 454 | % | 0 - 100 %
2075 | FastHeatT | PAR - Recovery - Startup Time [sec.] | UINT | ReadWrite | HoldingRegister | 455 | sec.
2076 | FastHeatThrsh | PAR - Recovery - Heating Limit [%] | REAL | ReadWrite | HoldingRegister | 456 | % | 0 - 100 %
2078 | FilterF7_Max | PAR - Filter - Maximum pressure F7 [Pa] | REAL | ReadWrite | HoldingRegister | 457 | Pa
2079 | FilterF9_Max | PAR - Filter - Maximum pressure F9 [Pa] | REAL | ReadWrite | HoldingRegister | 458 | Pa
2080 | FilterPG4_Max | PAR - Filter - Maximum pressure PG4 [Pa] | REAL | ReadWrite | HoldingRegister | 459 | Pa
2081 | FilterRet_Type | PAR - Filter - Return type | INT | ReadWrite | HoldingRegister | 460 |  | 0 - None 1 - PG4/G4 2 - M5/F7 3 - F9
2082 | FilterSup_Type | PAR - Filter - Supply type | INT | ReadWrite | HoldingRegister | 461 |  | 0 - None 1 - PG4/G4 2 - M5/F7 3 - F9
2083 | FireExhSpeed | PAR - Fan - Fire Setting - Return Speed [%] | REAL | ReadWrite | HoldingRegister | 462 | % | 0 - 100 %
2084 | FireSupplySpeed | PAR - Fan - Fire Setting - Supply Speed [%] | REAL | ReadWrite | HoldingRegister | 463 | % | 0 - 100 %
2085 | FireThrsh | PAR - Fan - Fire Setting - Threshold [°C] | REAL | ReadWrite | HoldingRegister | 464 | °C
2098 | HE_Pwr[0] | PAR - Heating - Main Heater - Maximum Power Modulating [%] | REAL | ReadWrite | HoldingRegister | 465 | % | 0 - 100 %
2099 | HE_Pwr[1] | PAR - Heating - Main Heater - Maximum Power 1 Stage [%] | REAL | ReadWrite | HoldingRegister | 466 | % | 0 - 100 %
2100 | HE_Pwr[2] | PAR - Heating - Main Heater - Maximum Power 2 Stage [%] | REAL | ReadWrite | HoldingRegister | 467 | % | 0 - 100 %
2102 | Heat_2.Man | PAR - Heating - Main Device 2 - Manual Digital | USINT | ReadWrite | HoldingRegister | 468 |  | 0 - AUTO 1 - OFF 2 - ON
2103 | HeatExtTempThrsh | PAR - Regulation - ChangeOver - External Temperature - Heat Threshold [°C] | REAL | ReadWrite | HoldingRegister | 469 | °C
2104 | HeatMinOffT | PAR - Heating - Main Heater DX - Time - Minimum OFF [sec.] | UINT | ReadWrite | HoldingRegister | 470 | sec.
2105 | HeatMinOnOnSameT | PAR - Heating - Main Heater DX - Time - Between starts [sec.] | UINT | ReadWrite | HoldingRegister | 471 | sec.
2106 | HeatMinOnT | PAR - Heating - Main Heater DX - Time - Minimum ON [sec.] | UINT | ReadWrite | HoldingRegister | 472 | sec.
2107 | HeatRecovery.Man | PAR - Recovery - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 473 | % | 0 - 100 %
2108 | HeatVlv.Man | PAR - Heating - Main Heater - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 474 | % | 0 - 100 %
2110 | Hum.Man | PAR - Humidity - Manual Digital | USINT | ReadWrite | HoldingRegister | 475 |  | 0 - AUTO 1 - OFF 2 - ON
2111 | Hum_PID.DeadBand | PAR - Regulation PID - Humidity - DeadBand [g/m3] | REAL | ReadWrite | HoldingRegister | 476 | g/m3
2112 | Hum_PID.Kp | PAR - Regulation PID - Humidity - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 477 | Kp
2113 | Hum_PID.Ti | PAR - Regulation PID - Humidity - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 478 | Ti - sec.
2114 | HW_Set | PAR - Heating - Main Water - SetPoint [°C] | REAL | ReadWrite | HoldingRegister | 479 | °C
2115 | IdleT_ExhFan | PAR - Fan - Return - Idle Time [sec.] | UINT | ReadWrite | HoldingRegister | 480 | sec.
2116 | IdleT_SupplyFan | PAR - Fan - Supply - Idle Time [sec.] | UINT | ReadWrite | HoldingRegister | 481 | sec.
2117 | K_FactorExh | PAR - Fan - Return - K-Factor | REAL | ReadWrite | HoldingRegister | 482
2118 | K_FactorExhCode | PAR - Fan - Return - Fan Code | USINT | ReadWrite | HoldingRegister | 483 |  | 0 - CUSTOM 1 - VS-225 2 - VS-250 3 - VS-315 4 - VS-355 5 - VS-400 6 - VS-450 7 - VS-500 8 - VS-560 9 - VS-630
2119 | K_FactorSupply | PAR - Fan - Supply - K-Factor | REAL | ReadWrite | HoldingRegister | 484
2120 | K_FactorSupplyCode | PAR - Fan - Supply - Fan Code | USINT | ReadWrite | HoldingRegister | 485 |  | 0 - CUSTOM 1 - VS-225 2 - VS-250 3 - VS-315 4 - VS-355 5 - VS-400 6 - VS-450 7 - VS-500 8 - VS-560 9 - VS-630
2121 | LowSupplyTempThrsh | PAR - Heating - Supply Limit - Threshold [°C] | REAL | ReadWrite | HoldingRegister | 486 | °C
2122 | MainCoolMin | PAR - Cooling - Main Cooler - Minimum Power [%] | REAL | ReadWrite | HoldingRegister | 487 | % | 0 - 100 %
2123 | MainCW_MinPID | PAR - Cooling - Main Cooler Water - Minimum Valve Signal [%] | REAL | ReadWrite | HoldingRegister | 488 | % | 0 - 100 %
2124 | MainHeatMin | PAR - Heating - Main Heater - Minimum Power [%] | REAL | ReadWrite | HoldingRegister | 489 | % | 0 - 100 %
2125 | MainHW_MinPID | PAR - Heating - Main Water - Minimum Valve Singal [%] | REAL | ReadWrite | HoldingRegister | 490 | % | 0 - 100 %
2126 | ManExhFanIdle | PAR - Fan - Return - Idle Power [%] | REAL | ReadWrite | HoldingRegister | 491 | % | 0 - 100 %
2127 | ManSupplyFanIdle | PAR - Fan - Supply - Idle Power [%] | REAL | ReadWrite | HoldingRegister | 492 | % | 0 - 100 %
2128 | MinHeatRec | PAR - Recovery - Heating - Minimum Power [%] | REAL | ReadWrite | HoldingRegister | 493 | % | 0 - 100 %
2129 | ModulHum.Man | PAR - Humidity - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 494 | % | 0 - 100 %
2130 | ModulMixDamp.Man | PAR - Mix Damper - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 495 | % | 0 - 100 %
2131 | ModulMixDampMaxVal | PAR - Mix Damper - Limits - Maximum Openning [%] | REAL | ReadWrite | HoldingRegister | 496 | % | 0 - 100 %
2132 | ModulMixDampMinVal | PAR - Mix Damper - Limits - Minimum Openning [%] | REAL | ReadWrite | HoldingRegister | 497 | % | 0 - 100 %
2133 | ModulPreHeat.Man | PAR - Heating - PreHeating - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 498 | % | 0 - 100 %
2134 | NightKickHour | PAR - System - Night Kick Time - Hour [h] | UINT | ReadWrite | HoldingRegister | 499 | h
2135 | NightKickMinute | PAR - System - Night Kick Time - Minute [min.] | UINT | ReadWrite | HoldingRegister | 500 | min.
2136 | PID_Exh.Kp | PAR - Regulation PID - Fan Return - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 501 | Kp
2137 | PID_Exh.Td | PAR - Regulation PID - Fan Return - Derivative time [Td - sec.] | UINT | ReadWrite | HoldingRegister | 502 | Td - sec.
2138 | PID_Exh.Ti | PAR - Regulation PID - Fan Return - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 503 | Ti - sec.
2139 | PID_FrostProt.Kp | PAR - Regulation PID - Recovery - Frost - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 504 | Kp
2140 | PID_FrostProt.SetP | PAR - Recovery - Frost Protection - SetPoint [°C] | REAL | ReadWrite | HoldingRegister | 505 | °C
2141 | PID_FrostProt.Ti | PAR - Regulation PID - Recovery - Frost - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 506 | Ti - sec.
2142 | PID_HeatHW.Kp | PAR - Regulation PID - Main Water - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 507 | Kp
2143 | PID_HeatHW.Ti | PAR - Regulation PID - Main Water - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 508 | Ti - sec.
2144 | PID_PreHeatCoil.Kp | PAR - Regulation PID - PreHeating - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 509 | Kp
2145 | PID_PreHeatCoil.Ti | PAR - Regulation PID - PreHeating - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 510 | Ti - sec.
2146 | PID_PreHeatHW.Kp | PAR - Regulation PID - PreHeater Water - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 511 | Kp
2147 | PID_PreHeatHW.Ti | PAR - Regulation PID - PreHeater Water - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 512 | Ti - sec.
2148 | PID_Supply.Kp | PAR - Regulation PID - Fan Supply - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 513 | Kp
2149 | PID_Supply.Td | PAR - Regulation PID - Fan Supply - Derivative time [Td - sec.] | UINT | ReadWrite | HoldingRegister | 514 | Td - sec.
2150 | PID_Supply.Ti | PAR - Regulation PID - Fan Supply - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 515 | Ti - sec.
2152 | PreHeaterPump.Man | PAR - Heating - PreHeating - Manual Digital | USINT | ReadWrite | HoldingRegister | 516 |  | 0 - AUTO 1 - OFF 2 - ON
2153 | PreHeatHE_Pwr[0] | PAR - Heating - PreHeating - Maximum Power Modulating [%] | REAL | ReadWrite | HoldingRegister | 517 | % | 0 - 100 %
2154 | PreHeatHE_Pwr[1] | PAR - Heating - PreHeating - Maximum Power 1 Stage [%] | REAL | ReadWrite | HoldingRegister | 518 | % | 0 - 100 %
2155 | PreHeatMin | PAR - Heating - PreHeating - Minimum Power [%] | REAL | ReadWrite | HoldingRegister | 519 | % | 0 - 100 %
2156 | PreHeatMinOffT | PAR - Heating - PreHeating DX - Time - Minimum OFF [sec.] | UINT | ReadWrite | HoldingRegister | 520 | sec.
2157 | PreheatMinOnOnSameT | PAR - Heating - PreHeating DX - Time - Between starts [sec.] | UINT | ReadWrite | HoldingRegister | 521 | sec.
2158 | PreHeatMinOnT | PAR - Heating - PreHeating DX - Time - Minimum ON [sec.] | UINT | ReadWrite | HoldingRegister | 522 | sec.
2159 | PreHeatRotConf.DevNoPerCirc | PAR - Heating - PreHeating - Type | INT | ReadWrite | HoldingRegister | 523 |  | 1 - MODULATING 2 - MOD. + 1 STAGE
2160 | PreHeatSet | PAR - Heating - PreHeater Water - SetPoint [°C] | REAL | ReadWrite | HoldingRegister | 524 | °C
2161 | PreHW_MinPID | PAR - Heating - PreHeater Water - Minimum Valve Signal [%] | REAL | ReadWrite | HoldingRegister | 525 | % | 0 - 100 %
2162 | Rec_MinPID | PAR - Recovery - Heating - Minimum Recovery [%] | REAL | ReadWrite | HoldingRegister | 526 | % | 0 - 100 %
2164 | RecoveryPump.Man | PAR - Recovery - Manual Digital | USINT | ReadWrite | HoldingRegister | 527 |  | 0 - AUTO 1 - OFF 2 - ON
2166 | ReHeat.Man | PAR - Heating - ReHeating - Manual Digital | USINT | ReadWrite | HoldingRegister | 528 |  | 0 - AUTO 1 - OFF 2 - ON
2167 | ReHeatHE_Pwr[0] | PAR - Heating - ReHeating - Maximum Power Modulating [%] | REAL | ReadWrite | HoldingRegister | 529 | % | 0 - 100 %
2168 | ReHeatHE_Pwr[1] | PAR - Heating - ReHeating - Maximum Power 1 Stage [%] | REAL | ReadWrite | HoldingRegister | 530 | % | 0 - 100 %
2169 | ReHeatMin | PAR - Heating - ReHeating - Minimum Power [%] | REAL | ReadWrite | HoldingRegister | 531 | % | 0 - 100 %
2170 | ReHeatMinOffT | PAR - Heating - ReHeater DX - Time - Minimum OFF [sec.] | UINT | ReadWrite | HoldingRegister | 532 | sec.
2171 | ReHeatMinOnOnSameT | PAR - Heating - ReHeater DX - Time - Between starts [sec.] | UINT | ReadWrite | HoldingRegister | 533 | sec.
2172 | ReHeatMinOnT | PAR - Heating - ReHeater DX - Time - Minimum ON [sec.] | UINT | ReadWrite | HoldingRegister | 534 | sec.
2173 | ReHeatRotConf.CompMinPwr | PAR - Heating - ReHeating - Minimum Power [%] | INT | ReadWrite | HoldingRegister | 535 | % | 0 - 100 %
2174 | ReHeatRotConf.DevNoPerCirc | PAR - Heating - ReHeating - Type | INT | ReadWrite | HoldingRegister | 536 |  | 1 - MODULATING 2 - MOD. + 1 STAGE
2175 | ReHeatVlv.Man | PAR - Heating - ReHeating - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 537 | % | 0 - 100 %
2176 | ReHW_MinPID | PAR - Heating - ReHeating - Minimum Valve Signal [%] | REAL | ReadWrite | HoldingRegister | 538 | % | 0 - 100 %
2177 | Ret_NrPole | PAR - Fan - Return - Number of pole | REAL | ReadWrite | HoldingRegister | 539
2179 | RevOut_1.Man | PAR - Heating - Reverse Device 1 - Manual Digital | USINT | ReadWrite | HoldingRegister | 540 |  | 0 - AUTO 1 - OFF 2 - ON
2181 | RevOut_2.Man | PAR - Heating - Reverse Device 2 - Manual Digital | USINT | ReadWrite | HoldingRegister | 541 |  | 0 - AUTO 1 - OFF 2 - ON
2182 | RevOutVlv.Man | PAR - Heating - Reverse Device 1 - Manual Analog [%] | USINT | ReadWrite | HoldingRegister | 542 | % | 0 - 100 %
2183 | RoomReg_SetP_Offs_Kp | PAR - Regulation PID - Room Compnsation - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 543 | Kp
2184 | RoomReg_SetP_Offs_Ti | PAR - Regulation PID - Room Compnsation - Integral time [sec.] | UINT | ReadWrite | HoldingRegister | 544 | sec.
2185 | RotConf.CompMinPwr | PAR - Heating - Main Heater - Minimum Power [%] | INT | ReadWrite | HoldingRegister | 545 | % | 0 - 100 %
2186 | RotConf.DevNoPerCirc | PAR - Heating - Main Heater - Type | INT | ReadWrite | HoldingRegister | 546 |  | 1 - MODULATING 2 - MOD. + 1 STAGE 3 - MOD. + 2 STAGES
2187 | RRG_NrPole | PAR - Recovery - Rotary - Numver of pole | REAL | ReadWrite | HoldingRegister | 547
2188 | SetMaxLimit | PAR - Regulation - Limits - Return / Room - Maximum [°C] | REAL | ReadWrite | HoldingRegister | 548 | °C
2189 | SetMinLimit | PAR - Regulation - Limits - Return / Room - Minimum [°C] | REAL | ReadWrite | HoldingRegister | 549 | °C
2190 | StandbyT | PAR - System - StandBy - Time [sec.] | UDINT | ReadWrite | HoldingRegister | 550 | sec.
2191 | StartHumPerc | PAR - Humidity - Digital - Start [%] | REAL | ReadWrite | HoldingRegister | 551 | % | 0 - 100 %
2192 | StopHumPerc | PAR - Humidity - Digital - Stop [%] | REAL | ReadWrite | HoldingRegister | 552 | % | 0 - 100 %
2193 | Sup_NrPole | PAR - Fan - Supply - Number of pole | REAL | ReadWrite | HoldingRegister | 553
2194 | SupplyAirFlowSet_Msk | PAR - Fan - Return - Flow - Maximum [m3/h] | REAL | ReadWrite | HoldingRegister | 554 | m3/h
2195 | SupplyAirPSet_Msk | PAR - Fan - Supply - Pressure - Maximum [Pa] | REAL | ReadWrite | HoldingRegister | 555 | Pa
2196 | SupplyDewPoint | PAR - Humidity - Supply Dewpoint [°C] | REAL | ReadWrite | HoldingRegister | 556 | °C
2197 | SupplyFanMax | PAR - CO2 - Fan Compensation - Max Air-Flow Quality [%] | REAL | ReadWrite | HoldingRegister | 557 | % | 0 - 100 %
2198 | SupplyMaxSet | PAR - Regulation - Limits - Temperature Supply - Maximum [°C] | REAL | ReadWrite | HoldingRegister | 558 | °C
2199 | SupplyMinSet | PAR - Regulation - Limits - Temperature Supply - Minimum [°C] | REAL | ReadWrite | HoldingRegister | 559 | °C
2200 | SupplyTemp_CoolHeatDT | PAR - Regulation - ChangeOver - External Temperature - Time Delay [sec.] | UDINT | ReadWrite | HoldingRegister | 560 | sec.
2201 | ThrshOffCool_1 | PAR - Cooling - Main Cooler DX - Stop Step 1 [%] | REAL | ReadWrite | HoldingRegister | 561 | % | 0 - 100 %
2202 | ThrshOffCool_2 | PAR - Cooling - Main Cooler DX - Stop Step 2 [%] | REAL | ReadWrite | HoldingRegister | 562 | % | 0 - 100 %
2203 | ThrshOffHeat_1 | PAR - Heating - Main Heater DX - Stop Step 1 [%] | REAL | ReadWrite | HoldingRegister | 563 | % | 0 - 100 %
2204 | ThrshOffHeat_2 | PAR - Heating - Main Heater DX - Stop Step 2 [%] | REAL | ReadWrite | HoldingRegister | 564 | % | 0 - 100 %
2205 | ThrshOnCool_1 | PAR - Cooling - Main Cooler DX - Start Step 1 [%] | REAL | ReadWrite | HoldingRegister | 565 | % | 0 - 100 %
2206 | ThrshOnCool_2 | PAR - Cooling - Main Cooler DX - Start Step 2 [%] | REAL | ReadWrite | HoldingRegister | 566 | % | 0 - 100 %
2207 | ThrshOnHeat_1 | PAR - Heating - Main Heater DX - Start Step 1 [%] | REAL | ReadWrite | HoldingRegister | 567 | % | 0 - 100 %
2208 | ThrshOnHeat_2 | PAR - Heating - Main Heater DX - Start Step 2 [%] | REAL | ReadWrite | HoldingRegister | 568 | % | 0 - 100 %
2209 | W_HeatFreezeSet | PAR - Heating - Main Water - Frreeze SetPoint [°C] | REAL | ReadWrite | HoldingRegister | 569 | °C
2210 | W_PreHeatFreezeSet | PAR - Heating - PreHeater Water - Freeze SetPoint [°C] | REAL | ReadWrite | HoldingRegister | 570 | °C
2211 | WakeUpT | PAR - System - Wake Up - Time [sec.] | UDINT | ReadWrite | HoldingRegister | 571 | sec.
2212 | WarnThrshExhFlw_Msk | PAR - Fan - Return - Warning Threshold Air Flow [m3/h] | REAL | ReadWrite | HoldingRegister | 572 | m3/h
2213 | WarnThrshSupplyFlw_Msk | PAR - Fan - Supply - Warning Threshold Air Flow [m3/h] | REAL | ReadWrite | HoldingRegister | 573 | m3/h
2214 | AbsHum | PAR - Humidity - ABS Humidity [g/m3] | REAL | Read | HoldingRegister | 574 | g/m3
2215 | AbsHumSet | PAR - Humidity - ABS SetPoint [g/m3] | REAL | Read | HoldingRegister | 575 | g/m3
2216 | AfterPreHeatReq | PAR - Regulation PID - PreHeating - Output [%] | REAL | Read | HoldingRegister | 576 | % | 0 - 100 %
2217 | AirQualFan | PAR - Regulation PID - CO2 Fan Compensation - Output [%] | REAL | Read | HoldingRegister | 577 | % | 0 - 100 %
2218 | AirQualReq_1 | PAR - Regulation PID - CO2 Mixing - Output [%] | REAL | Read | HoldingRegister | 578 | % | 0 - 100 %
2219 | Cooling_PID_Seq[2] | PAR - Regulation PID - Recovery - Cooling - Output [%] | REAL | Read | HoldingRegister | 579 | % | 0 - 100 %
2220 | Cooling_PID_Seq[3] | PAR - Regulation PID - Reverse - Cooling - Output [%] | REAL | Read | HoldingRegister | 580 | % | 0 - 100 %
2221 | Cooling_PID_Seq[4] | PAR - Regulation PID - Main Cooler - Output [%] | REAL | Read | HoldingRegister | 581 | % | 0 - 100 %
2222 | Cooling_PID_Seq[5] | PAR - Regulation PID - Mixing - Cooling - Output [%] | REAL | Read | HoldingRegister | 582 | % | 0 - 100 %
2223 | FrostProtReq | PAR - Regulation PID - Recovery - Frost - Output [%] | REAL | Read | HoldingRegister | 583 | % | 0 - 100 %
2224 | Heating_PID_Seq[2] | PAR - Regulation PID - Recovery - Heating - Output [%] | REAL | Read | HoldingRegister | 584 | % | 0 - 100 %
2225 | Heating_PID_Seq[3] | PAR - Regulation PID - Reverse - Heating - Output [%] | REAL | Read | HoldingRegister | 585 | % | 0 - 100 %
2226 | Heating_PID_Seq[4] | PAR - Regulation PID - Main Heater - Output [%] | REAL | Read | HoldingRegister | 586 | % | 0 - 100 %
2227 | Heating_PID_Seq[5] | PAR - Regulation PID - Mixing - Heating - Output [%] | REAL | Read | HoldingRegister | 587 | % | 0 - 100 %
2228 | Heating_PID_Seq[6] | PAR - Regulation PID - ReHeating - Output [%] | REAL | Read | HoldingRegister | 588 | % | 0 - 100 %
2229 | Heating_PID_Seq[7] | PAR - Regulation PID - Fan Heating - Output [%] | REAL | Read | HoldingRegister | 589 | % | 0 - 100 %
2230 | HumDehumReq | PAR - Regulation PID - Humidity - Output [%] | REAL | Read | HoldingRegister | 590 | % | 0 - 100 %
2231 | HW_AfreezeReq | PAR - Regulation PID - Main Water - Output [%] | REAL | Read | HoldingRegister | 591 | % | 0 - 100 %
2232 | PID_DewCompens | PAR - Regulation PID - Humidity - Dewpoint - Output [%] | REAL | Read | HoldingRegister | 592 | % | 0 - 100 %
2233 | PID_RegCompens | PAR - Regulation PID - Room Compnsation - Output [%] | REAL | Read | HoldingRegister | 593 | % | 0 - 100 %
2234 | PreW_AfreezeReq | PAR - Regulation PID - PreHeater Water - Output [%] | REAL | Read | HoldingRegister | 594 | % | 0 - 100 %
2235 | MainHeatMax | PAR - Heating - Main Heater - Maximum Power [%] | REAL | ReadWrite | HoldingRegister | 595 | % | 0 - 100 %
2236 | RevHeat_Sig_Min | PAR - Heating - Reverse Device 1 - Heating - Minimum signal [%] | REAL | ReadWrite | HoldingRegister | 596 | % | 0 - 100 %
2237 | RevHeat_Sig_Max | PAR - Heating - Reverse Device 1 - Heating - Maximum signal [%] | REAL | ReadWrite | HoldingRegister | 597 | % | 0 - 100 %
2238 | RevCool_Sig_Min | PAR - Heating - Reverse Device 1 - Cooling - Minimum signal [%] | REAL | ReadWrite | HoldingRegister | 598 | % | 0 - 100 %
2239 | RevCool_Sig_Max | PAR - Heating - Reverse Device 1 - Cooling - Maximum signal [%] | REAL | ReadWrite | HoldingRegister | 599 | % | 0 - 100 %
2240 | RevTemp_En | PAR - Heating - Reverse Device 1 - Permistion from external temperature [°C] | REAL | ReadWrite | HoldingRegister | 600 | °C
2241 | ReHeatMax | PAR - Heating - ReHeating - Maximum Power [%] | REAL | ReadWrite | HoldingRegister | 601 | % | 0 - 100 %
2242 | PreHeatMax | PAR - Heating - PreHeating - Maximum Power [%] | REAL | ReadWrite | HoldingRegister | 602 | % | 0 - 100 %
2243 | LowTempAlrmDT_Run | PAR - Heating - Supply Limit - Threshold delay [sec.] | UINT | ReadWrite | HoldingRegister | 603 | sec.
2246 | MainStartupValue | PAR - Heating - Main Heater HW - Pre-Heat always start - Minimum signal [%] | REAL | ReadWrite | HoldingRegister | 604 | % | 0 - 100 %
2247 | HE_Alarm_Delay | PAR - Heating - Main Heater HE - Alarm delay [sec.] | UDINT | ReadWrite | HoldingRegister | 605 | sec.
2248 | Pump_ExtTemp | PAR - Heating - Main Heater HW - Active pump when external temp lower [°C] | REAL | ReadWrite | HoldingRegister | 606 | °C
2249 | Valve_ExtTemp | PAR - Heating - Main Heater HW - Active vavlve when external temp lower [°C] | REAL | ReadWrite | HoldingRegister | 607 | °C
2250 | MainHW_MinPID_Text | PAR - Heating - Main Heater HW - Minimum signal for winter valve [%] | REAL | ReadWrite | HoldingRegister | 608 | % | 0 - 100 %
2251 | FanFlowAlarm_Delay | PAR - Fan - Supply - Warning Threshold Pressure delay [sec.] | DINT | ReadWrite | HoldingRegister | 609 | sec.
2252 | DoubleFanRotT | PAR - Fan - Redundant - Time rotation [h] | USINT | ReadWrite | HoldingRegister | 610 | h
2254 | DoubleDamp.Man | PAR - Fan - Redundant - Manual Digital | USINT | ReadWrite | HoldingRegister | 611 |  | 0 - AUTO 1 - OFF 2 - ON
2256 | FanTempReg_Sig | PAR - Fan - Temperature regulation - Output [%] | REAL | ReadWrite | HoldingRegister | 612 | % | 0 - 100 %
2257 | DevCfg_PID_Seq_Heat[7].Kp | PAR - Fan - Temperature regulation - Proportional gain [Kp] | REAL | ReadWrite | HoldingRegister | 613 | Kp
2258 | DevCfg_PID_Seq_Heat[7].Ti | PAR - Fan - Temperature regulation - Integral time [Ti - sec.] | UINT | ReadWrite | HoldingRegister | 614 | Ti - sec.
2259 | FanTempReg_Max | PAR - Fan - Temperature regulation - Maximum fan signal correction [%] | REAL | ReadWrite | HoldingRegister | 615 | % | 0 - 100 %
2262 | RRG_MinValueFor_Al | PAR - Recovery - Rotery - Minium signal for active power [%] | REAL | ReadWrite | HoldingRegister | 616 | % | 0 - 100 %
2263 | RRG_MinPower_Al | PAR - Recovery - Rotery - Minimum power for alarm [W] | REAL | ReadWrite | HoldingRegister | 617 | W
2264 | RRG_Alarm_Delay | PAR - Recovery - Rotery - Dlarm delay [sec.] | DINT | ReadWrite | HoldingRegister | 618 | sec.
2266 | Mix_Val_ECO | PAR - Mixing - Manual mode ECO - Signal [%] | REAL | ReadWrite | HoldingRegister | 619 | % | 0 - 100 %
2268 | Mix_Val_OPTIMAL | PAR - Mixing - Manual mode Optimal - Signal [%] | REAL | ReadWrite | HoldingRegister | 620 | % | 0 - 100 %
2270 | Mix_Val_COMFORT | PAR - Mixing - Manual mode Comfort - Signal [%] | REAL | ReadWrite | HoldingRegister | 621 | % | 0 - 100 %
2271 | AFreezeHeatOut | PAR - Heater - Antifreeze - Output [%] | REAL | ReadWrite | HoldingRegister | 622 | % | 0 - 100 %
2272 | AFreezeHeatOutT | PAR - Heater - Antifreeze - Output T [%] | UINT | ReadWrite | HoldingRegister | 623 | % | 0 - 100 %
2273 | __SYSVA_BEEP_ON | SYS - Hardware - Activate Buzzer for a while | USINT | ReadWrite | HoldingRegister | 624 |  | Virtual HMI
2274 | __SYSVA_CURSOR_COLUMN | SYS - Hardware - Display cursor current X coordinate | INT | ReadWrite | HoldingRegister | 625 |  | Virtual HMI
2275 | __SYSVA_CURSOR_ROW | SYS - Hardware - Display cursor current Y coordinate | INT | ReadWrite | HoldingRegister | 626 |  | Virtual HMI
2276 | __SYSVA_CURSOR_VAR | SYS - Hardware - Display cursor for scrolling lists | INT | ReadWrite | HoldingRegister | 627 |  | Virtual HMI
2277 | __SYSVA_KEY_COUNTER | SYS - Hardware - Key pressed time | INT | ReadWrite | HoldingRegister | 628 |  | Virtual HMI
2278 | __SYSVA_KEY_PRESSED | SYS - Hardware - Key pressed flag | USINT | ReadWrite | HoldingRegister | 629 |  | Virtual HMI
2279 | __SYSVA_MANUAL_BUZZER_OFF | SYS - Hardware - Deactivates the alarm buzzer | USINT | ReadWrite | HoldingRegister | 630 |  | Virtual HMI
2280 | __SYSVA_MANUAL_BUZZER_ON | SYS - Hardware - Activate Buzzer when controlled manually | USINT | ReadWrite | HoldingRegister | 631 |  | Virtual HMI
2281 | __SYSVA_TMP_VALUE | SYS - Hardware - Temp value for field editing | UDINT | ReadWrite | HoldingRegister | 632 |  | Virtual HMI
2283 | AfterPreHeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - After PreHeat [°C] | USINT | ReadWrite | HoldingRegister | 633 | °C | 0 - AUTO OR 1 - 100%
2284 | AfterPreHeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - After PreHeat [°C] | REAL | ReadWrite | HoldingRegister | 634 | °C
2285 | AppCode_Board | SYS - Application Code - Board - _ _ - _ . _ . _ . _ . _ . _ . _ . X | USINT | ReadWrite | HoldingRegister | 635 |  | 0 - uPC3 XS 1 - uPC3 XS 2 - uPC3 Small 3 - uPC3 XS 4 - uPC3 XS 5 - uPC3 XS 6 - uPC3 XS
2286 | AppCode_Cool | SYS - Application Code - Cooling - _ _ - _ . X . _ . _ . _ . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 636 |  | 0 - None 1 - Chilled water 2 - DX
2287 | AppCode_Eco | SYS - Application Code - ECO - _ _ - _ . _ . _ . _ . _ . X . _ . _ | USINT | ReadWrite | HoldingRegister | 637 |  | 0 - NO 1 - YES
2288 | AppCode_Heat | SYS - Application Code - Heating - _ _ - X . _ . _ . _ . _ . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 638 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater 4 - Steam
2289 | AppCode_Hum | SYS - Application Code - Humidity - _ _ - _ . _ . _ . _ . _ . _ . X . _ | USINT | ReadWrite | HoldingRegister | 639 |  | 0 - None 1 - Evaporative 2 - Steam
2290 | AppCode_PreHeat | SYS - Application Code - PreHeating - _ _ - _ . _ . _ . X . _ . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 640 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater
2291 | AppCode_Rec | SYS - Application Code - Recirculation - XX - _ . _ . _ . _ . _ . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 641 |  | 0 - AS:Supply 1 - AD: S+E 2 - AR: S/E & Rotary 3 - AP: S/E + Cross 4 - AG: S/E + Glycol 5 - AX: S/E+HeatPump 6 - AE: Exhaust
2292 | AppCode_ReHeat | SYS - Application Code - Recirculation Heating - _ _ - _ . _ . _ . _ . X . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 642 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater
2293 | AppCode_Rev | SYS - Application Code - Rev - _ _ - _ . _ . X . _ . _ . _ . _ . _ | USINT | ReadWrite | HoldingRegister | 643 |  | 0 - None 1 - Hydronic 2 - DX
2303 | AppHumReg | SYS - Unit Configuration - Humidity Regulation | USINT | ReadWrite | HoldingRegister | 644 |  | 0 - NONE 1 - SUPPLY 2 - RETURN 3 - ROOM
2324 | AppTempReg | SYS - Unit Configuration - Temperature Regulation | USINT | ReadWrite | HoldingRegister | 645 |  | 0 - SUPPLY 1 - RETURN 2 - ROOM
2326 | BMS_Addr | SYS - Unit Configuration - BMS port - Address | USINT | ReadWrite | HoldingRegister | 646 |  | 1 - 32
2328 | CO2_Simulation_Var | SYS - IO Setting - CO2 Simulate - Value [ppm] | INT | ReadWrite | HoldingRegister | 647 | ppm
2330 | CoolAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Cool | USINT | ReadWrite | HoldingRegister | 648 |  | 0 - AUTO 1 - OFF 2 - ON
2331 | DriveTyp | SYS - Unit Configuration - Import / Export - Memory Type | BYTE | ReadWrite | HoldingRegister | 649 |  | 0 - FLASH MEMORY 1 - USB
2340 | ExhFanRegTyp | SYS - Unit Configuration - Regulation Return | USINT | ReadWrite | HoldingRegister | 650 |  | 0 - NONE 1 - VAV 2 - CAV
2341 | ExhMulti | SYS - Unit Configuration - Config Return | USINT | ReadWrite | HoldingRegister | 651 |  | 0 - 1 FAN 1 - REDUNDANT 2 - 2 FANS 3 - 3 FANS 4 - 4 FANS 5 - 5 FANS 6 - 6 FANS 7 - 7 FANS 8 - 8 FANS 9 - 9 FANS 10 - 10 FANS
2342 | ExhTemp.Man | SYS - IO Setting - Manual - Temperature Exhaust [°C] | USINT | ReadWrite | HoldingRegister | 652 | °C | 0 - AUTO OR 1 - 100%
2343 | ExhTemp.Offset | SYS - IO Setting - Offset - Temperature Exhaust [°C] | REAL | ReadWrite | HoldingRegister | 653 | °C
2345 | ExtTemp.Man | SYS - IO Setting - Manual - Temperature - External [°C] | USINT | ReadWrite | HoldingRegister | 654 | °C | 0 - AUTO OR 1 - 100%
2346 | ExtTemp.Offset | SYS - IO Setting - Offset - Temperature - External [°C] | REAL | ReadWrite | HoldingRegister | 655 | °C
2347 | FB_Baud_msk | SYS - Unit Configuration - FieldBus Port - Baudrate | INT | ReadWrite | HoldingRegister | 656 |  | 0 - 4800 1 - 9600 2 - 19200 3 - 38400
2349 | FireAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm Fire | USINT | ReadWrite | HoldingRegister | 657 |  | 0 - AUTO 1 - OFF 2 - ON
2352 | HumAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Humidifier | USINT | ReadWrite | HoldingRegister | 658 |  | 0 - AUTO 1 - OFF 2 - ON
2354 | ID2_Alrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Heat | USINT | ReadWrite | HoldingRegister | 659 |  | 0 - AUTO 1 - OFF 2 - ON
2355 | ImpExpFileName | SYS - Unit Configuration - Import / Export - File Name | INT | ReadWrite | HoldingRegister | 660 |  | 0 - 99
2356 | LangChange | SYS - Unit Configuration - Language | DINT | ReadWrite | HoldingRegister | 661 |  | 0 - EN 1 - PL
2357 | MinFanPwrRet | SYS - Unit Configuration - Minimum Speed - Return [%] | REAL | ReadWrite | HoldingRegister | 662 | % | 0 - 100 %
2358 | MinFanPwrSup | SYS - Unit Configuration - Minimum Speed - Supply [%] | REAL | ReadWrite | HoldingRegister | 663 | % | 0 - 100 %
2359 | OffTotMinutes | SYS - Hardware - Time last blackout [min.] | UINT | ReadWrite | HoldingRegister | 664 | min.
2360 | OnOffStatus | SYS - Hardware - Machine Status [msec.] | USINT | ReadWrite | HoldingRegister | 665 | msec.
2361 | PrgCycleMs | SYS - Hardware - Cycle [msec.] | UINT | ReadWrite | HoldingRegister | 666 | msec.
2363 | RecSupplyTemp.Man | SYS - IO Setting - Manual - Temperature - Supply Recovery [°C] | USINT | ReadWrite | HoldingRegister | 667 | °C | 0 - AUTO OR 1 - 100%
2364 | RecSupplyTemp.Offset | SYS - IO Setting - Offset - Temperature - Supply Recovery [°C] | REAL | ReadWrite | HoldingRegister | 668 | °C
2366 | RemoteOn.Man | SYS - IO Setting - Digital Input - Manual - Remote ON | USINT | ReadWrite | HoldingRegister | 669 |  | 0 - AUTO 1 - OFF 2 - ON
2368 | RetFilter.Man | SYS - IO Setting - Digital Input - Manual - Filter - Return | USINT | ReadWrite | HoldingRegister | 670 |  | 0 - AUTO 1 - OFF 2 - ON
2370 | RetTemp.Man | SYS - IO Setting - Manual - Temperature - Return [°C] | USINT | ReadWrite | HoldingRegister | 671 | °C | 0 - AUTO OR 1 - 100%
2371 | RetTemp.Offset | SYS - IO Setting - Offset - Temperature - Return [°C] | REAL | ReadWrite | HoldingRegister | 672 | °C
2373 | SupplyFanRegTyp | SYS - Unit Configuration - Regulation Supply | USINT | ReadWrite | HoldingRegister | 673 |  | 0 - NONE 1 - VAV 2 - CAV
2375 | SupplyFilter.Man | SYS - IO Setting - Digital Input - Manual - Filter - Supply | USINT | ReadWrite | HoldingRegister | 674 |  | 0 - AUTO 1 - OFF 2 - ON
2376 | SupplyMulti | SYS - Unit Configuration - Config Supply | USINT | ReadWrite | HoldingRegister | 675 |  | 0 - 1 FAN 1 - REDUNDANT 2 - 2 FANS 3 - 3 FANS 4 - 4 FANS 5 - 5 FANS 6 - 6 FANS 7 - 7 FANS 8 - 8 FANS 9 - 9 FANS 10 - 10 FANS
2377 | SupplyTemp.Man | SYS - IO Setting - Manual - Temperature - Supply [°C] | USINT | ReadWrite | HoldingRegister | 676 | °C | 0 - AUTO OR 1 - 100%
2378 | SupplyTemp.Offset | SYS - IO Setting - Offset - Temperature - Supply [°C] | REAL | ReadWrite | HoldingRegister | 677 | °C
2379 | Typ_SP_CO2 | SYS - IO Setting - Modbus Probe Type - CO2 | USINT | ReadWrite | HoldingRegister | 678 |  | 0 - TYPE 1 1 - TYPE 2
2380 | Typ_SP_Hum | SYS - IO Setting - Modbus Probe Type - Humidity | USINT | ReadWrite | HoldingRegister | 679 |  | 0 - TYPE 1 1 - TYPE 2
2381 | Typ_SP_Pressure | SYS - IO Setting - Modbus Probe Type - Pressure | USINT | ReadWrite | HoldingRegister | 680 |  | 0 - TYPE 1 1 - TYPE 2
2382 | TypVFD | SYS - Unit Configuration - Supply Fan VFD Type | USINT | ReadWrite | HoldingRegister | 681 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2383 | TypVFD_2 | SYS - Unit Configuration - Return Fan VFD Type | USINT | ReadWrite | HoldingRegister | 682 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2384 | TypVFD_Rotor | SYS - Unit Configuration - Rotor Fan VFD Type | USINT | ReadWrite | HoldingRegister | 683 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2386 | Uom_Msk | SYS - Unit Configuration - Unit of Measure | DINT | ReadWrite | HoldingRegister | 684 |  | 1 - INTERNATIONAL 2 - USA
2388 | W_HeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - Water Heat [°C] | USINT | ReadWrite | HoldingRegister | 685 | °C | 0 - AUTO OR 1 - 100%
2389 | W_HeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - Water Heat [°C] | REAL | ReadWrite | HoldingRegister | 686 | °C
2391 | W_PreHeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - Water PreHeat [°C] | USINT | ReadWrite | HoldingRegister | 687 | °C | 0 - AUTO OR 1 - 100%
2392 | W_PreHeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - Water PreHeat [°C] | REAL | ReadWrite | HoldingRegister | 688 | °C
2395 | WinSum.Man | SYS - IO Setting - Digital Input - Manual - Winter / Summer | USINT | ReadWrite | HoldingRegister | 689 |  | 0 - AUTO 1 - OFF 2 - ON
2396 | CurrVer.D | SYS - System - Application Version - _ . _ . _ _ _ _ D D | UINT | Read | HoldingRegister | 690
2398 | CurrVer.X | SYS - System - Application Version - X . _ . _ _ _ _ _ _ | UINT | Read | HoldingRegister | 691
2399 | CurrVer.Y | SYS - System - Application Version - _ . Y . _ _ _ _ _ _ | UINT | Read | HoldingRegister | 692
2400 | CurrVer.Z | SYS - System - Application Version - _ . _ . Z Z Z _ _ _ | UINT | Read | HoldingRegister | 693
4765 | Reverse_Val_AO |  | UREAL16 |  | HoldingRegister | 694
4764 | UnitSetP.RoomTempSetP.StandBy |  | REAL16 |  | HoldingRegister | 695
4763 | UnitSetP.HumSetP.StandBy |  | REAL16 |  | HoldingRegister | 696
4762 | UnitSetP.AirQualitySetP.StandBy |  | REAL16 |  | HoldingRegister | 697
4761 | UnitSetP.AirFlwSetP.StandBy |  | REAL16 |  | HoldingRegister | 698
4760 | UnitSetP.RetAirFlwSetP.StandBy |  | REAL16 |  | HoldingRegister | 699
4759 | Heat_1.Man |  | UINT |  | HoldingRegister | 700
4758 | HC_Filter |  | UDINT |  | HoldingRegister | 701
4757 | HC_Filter_Limit |  | UDINT |  | HoldingRegister | 703
4756 | VFD_SupMax_RPM |  | UREAL16 |  | HoldingRegister | 705
4755 | VFD_RetMax_RPM |  | UREAL16 |  | HoldingRegister | 706
4754 | VFD_SupMax_Hz |  | UREAL16 |  | HoldingRegister | 707
4753 | VFD_RetMax_Hz |  | UREAL16 |  | HoldingRegister | 709
4752 | VFD_SupMax_RPM_2 |  | Int |  | HoldingRegister | 710
4751 | VFD_RetMax_RPM_2 |  | Int |  | HoldingRegister | 711
4750 | SupplyAirFlow_2 |  | INT |  | HoldingRegister | 712
4749 | ExhAirFlow_2 |  | INT |  | HoldingRegister | 713
4748 | SupplyAirFlowSet_2 |  | INT |  | HoldingRegister | 714
4747 | ExhAirFlowSet_2 |  | INT |  | HoldingRegister | 715
4746 | HC_SupplyFan_1.HrsRet |  | UDINT |  | HoldingRegister | 716
4745 | HC_ExhFan_1.HrsRet |  | UDINT |  | HoldingRegister | 718
4744 | HC_Heat_1.HrsRet |  | UDINT |  | HoldingRegister | 720
4743 | HC_Cool_1.HrsRet |  | UDINT |  | HoldingRegister | 722
4742 | Scheduler_OnOffUnit.Scheduler_1.Day | SCH - Scheduller - Time Band - Day | DINT | ReadWrite | HoldingRegister | 724 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN
4741 | SupplyTempSetP_RetComp |  | REAL16 |  | HoldingRegister | 726
4740 | Remote_Mode |  | Int |  | HoldingRegister | 728
4739 | MB_PressSupply_Adr |  | UDINT |  | HoldingRegister | 729
4738 | MB_PressSupply_Adr_2 |  | UDINT |  | HoldingRegister | 731
4737 | MB_PressSupply_Adr_3 |  | UDINT |  | HoldingRegister | 733
4736 | Pres_Filtr_Val |  | UREAL16 |  | HoldingRegister | 735
4735 | Pressure1_Simulation_Var |  | INT |  | HoldingRegister | 736
4734 | Pressure2_Simulation_Var |  | INT |  | HoldingRegister | 737
4733 | MB_PressReturn_Adr |  | UDINT |  | HoldingRegister | 738
4732 | MB_PressReturn_Adr_2 |  | UDINT |  | HoldingRegister | 740
4731 | SupHum_Offset |  | UREAL16 |  | HoldingRegister | 742
4730 | SupHum_Simulation_Var |  | UREAL16 |  | HoldingRegister | 743
4729 | RetHum_Offset |  | UREAL16 |  | HoldingRegister | 744
4728 | RetHum_Simulation_Var |  | UREAL16 |  | HoldingRegister | 746
4727 | CO2_Offset |  | UREAL16 |  | HoldingRegister | 747
4726 | Typ_FP_Pressure |  | UINT |  | HoldingRegister | 748
4725 | FilterSup_Type_2 |  | INT |  | HoldingRegister | 749
4724 | FilterSup_Type_3 |  | INT |  | HoldingRegister | 750
4723 | FilterRet_Type_2 |  | INT |  | HoldingRegister | 751
4722 | MainCoolMax |  | UREAL16 |  | HoldingRegister | 752
4721 | ExhAirDamp.Man |  | UINT |  | HoldingRegister | 754
4720 | PID_PreHeatCoil.SetP |  | REAL16 |  | HoldingRegister | 755
4719 | ReturnDewPoint |  | UREAL16 |  | HoldingRegister | 756
4718 | ExtTemp_Rec_En |  | REAL16 |  | HoldingRegister | 757
4717 | FanRecFrost |  | REAL16 |  | HoldingRegister | 758
4716 | FanRecFrost_Exh |  | REAL16 |  | HoldingRegister | 759
4715 | VAV_SupplySet |  | UREAL16 |  | HoldingRegister | 760
4714 | CAV_SupplySet |  | UREAL16 |  | HoldingRegister | 761
4713 | VAV_RetSet |  | UREAL16 |  | HoldingRegister | 762
4712 | CAV_RetSet |  | UREAL16 |  | HoldingRegister | 764
4711 | PollingTime |  | UDINT |  | HoldingRegister | 765
4710 | PwdUser |  | UINT |  | HoldingRegister | 767
4709 | PwdService |  | UINT |  | HoldingRegister | 768
4708 | PwdManuf |  | UINT |  | HoldingRegister | 769
4707 | BrowseAuth.RemotePwd |  | INT |  | HoldingRegister | 770
4706 | DevCfg_PID_Seq_Heat[8].Kp |  | UREAL16 |  | HoldingRegister | 771
4705 | DevCfg_PID_Seq_Heat[8].Ti |  | UINT |  | HoldingRegister | 773
4704 | HW_Set_Read |  | REAL16 |  | HoldingRegister | 774
4703 | HW_Set_X1 |  | REAL16 |  | HoldingRegister | 776
4702 | HW_Set_X2 |  | REAL16 |  | HoldingRegister | 778
4701 | FreezeAl_Text |  | REAL16 |  | HoldingRegister | 780
4700 | FreezeAl_Set |  | REAL16 |  | HoldingRegister | 782
4699 | HW_Set_Y2 |  | REAL16 |  | HoldingRegister | 783
4698 | HE_Fan_Delay |  | UDINT |  | HoldingRegister | 784
4697 | H_Time_On_Delay |  | UDINT |  | HoldingRegister | 786
4696 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Fan_Supply |  | REAL16 |  | HoldingRegister | 788
4695 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Fan_Return |  | REAL16 |  | HoldingRegister | 789
4694 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Filter_Supply |  | REAL16 |  | HoldingRegister | 790
4693 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Filter_Return |  | REAL16 |  | HoldingRegister | 791
4692 | SupFilter_Warning |  | UREAL16 |  | HoldingRegister | 792
4691 | RetFilter_Warning |  | UREAL16 |  | HoldingRegister | 793
4690 | FanSup_AI_X1 |  | UREAL16 |  | HoldingRegister | 794
4689 | FanSup_AI_X2 |  | UREAL16 |  | HoldingRegister | 795
4688 | FanSup_AI_Y1 |  | UREAL16 |  | HoldingRegister | 796
4687 | FanSup_AI_Y2 |  | UREAL16 |  | HoldingRegister | 797
4686 | FanRet_AI_X1 |  | UREAL16 |  | HoldingRegister | 798
4685 | FanRet_AI_X2 |  | UREAL16 |  | HoldingRegister | 799
4684 | FanRet_AI_Y1 |  | UREAL16 |  | HoldingRegister | 800
4683 | FanRet_AI_Y2 |  | UREAL16 |  | HoldingRegister | 801
4682 | MB_Devices.IO_PCB_1.AO1 |  | UREAL16 |  | HoldingRegister | 802
4681 | MB_Devices.IO_PCB_1.AO2 |  | UREAL16 |  | HoldingRegister | 804
4680 | MB_Devices.IO_PCB_1.AI1 |  | UREAL16 |  | HoldingRegister | 806
4679 | FanFlowAlarm_Delay | PAR - Fan - Supply - Warning Threshold Pressure delay [sec.] | DINT | ReadWrite | HoldingRegister | 807 | sec.
4678 | RRG_Alarm_Delay | PAR - Recovery - Rotery - Dlarm delay [sec.] | DINT | ReadWrite | HoldingRegister | 809 | sec.
4677 | BMS_Baud_msk |  | INT |  | HoldingRegister | 811
4676 | Scheduler_OnOffUnit.Scheduler_1.CurrDateTime_Sched.WkDay |  | UINT |  | HoldingRegister | 812
4675 | Scheduler_OnOffUnit.Scheduler_1.CopyTo_Day | SCH - Scheduller - Time Band - Copy to Day | UDINT | ReadWrite | HoldingRegister | 813 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN 7 - ALL
4674 | pLan_Modbus |  | UINT |  | HoldingRegister | 815
4673 | HMI_Alarm_code |  | INT |  | HoldingRegister | 816
4672 | HC_Heat_2.HrsRet |  | UDINT |  | HoldingRegister | 817
4671 | HC_Cool_2.HrsRet |  | UDINT |  | HoldingRegister | 819
4670 | HC_ReHeat.HrsRet |  | UDINT |  | HoldingRegister | 821
4669 | HC_RecoveryPump.HrsRet |  | UDINT |  | HoldingRegister | 823
4668 | HC_PreHeat.HrsRet |  | UDINT |  | HoldingRegister | 825
4667 | HC_Hum.HrsRet |  | UDINT |  | HoldingRegister | 827
4666 | FanTempReg_Sig_2 |  | REAL16 |  | HoldingRegister | 829
4665 | DevCfg_PID_Seq_Cool[6].Kp |  | UREAL16 |  | HoldingRegister | 831
4664 | DevCfg_PID_Seq_Cool[6].Ti |  | UINT |  | HoldingRegister | 833
4663 | FanTempReg_Max_2 |  | REAL16 |  | HoldingRegister | 834
4662 | MB_Press_FilterSup |  | UREAL16 |  | HoldingRegister | 835
4661 | MB_Press_FilterRet |  | UREAL16 |  | HoldingRegister | 836
4660 | SupplyAirP_Val_2 |  | UREAL16 |  | HoldingRegister | 837
4659 | SupplyAirP_Val_3 |  | UREAL16 |  | HoldingRegister | 838
4658 | ExhAirP_Val_2 |  | UREAL16 |  | HoldingRegister | 839
4657 | VAV_SupplyPID_Out |  | UREAL16 |  | HoldingRegister | 840
4656 | VAV_ExhPID_Out |  | UREAL16 |  | HoldingRegister | 841
4655 | CAV_SupplyPID_Out |  | UREAL16 |  | HoldingRegister | 842
4654 | CAV_ExhPID_Out |  | UREAL16 |  | HoldingRegister | 843
4653 | TempRegSetP |  | REAL16 |  | HoldingRegister | 844
4652 | Pressure3_Simulation_Var |  | INT |  | HoldingRegister | 845
4650 | Pressure4_Simulation_Var |  | INT |  | HoldingRegister | 846
4649 | Pressure5_Simulation_Var |  | INT |  | HoldingRegister | 847
4648 | Rec_ExtTemp |  | REAL16 |  | HoldingRegister | 848
4647 | Rec_MinExt |  | REAL16 |  | HoldingRegister | 849
4646 | Rec_MaxFrost |  | REAL16 |  | HoldingRegister | 850
4645 | Add_Temp_1 |  | REAL16 |  | HoldingRegister | 851
4644 | Add_Temp_2 |  | REAL16 |  | HoldingRegister | 852
4643 | Add_Temp_3 |  | REAL16 |  | HoldingRegister | 853
4642 | Add_Humid_1 |  | REAL16 |  | HoldingRegister | 854
4641 | Add_Humid_2 |  | REAL16 |  | HoldingRegister | 855
4640 | Add_Humid_3 |  | REAL16 |  | HoldingRegister | 856
4639 | Add_Adr_1 |  | UDINT |  | HoldingRegister | 857
4638 | Add_Adr_2 |  | UDINT |  | HoldingRegister | 859
4637 | Add_Adr_3 |  | UDINT |  | HoldingRegister | 861
4636 | VFD_SupChange_RPM |  | INT |  | HoldingRegister | 863
4635 | VFD_RetChange_RPM |  | INT |  | HoldingRegister | 864
4634 | MB_FanSupply_Adr_1 |  | UDINT |  | HoldingRegister | 866
4633 | MB_FanSupply_Adr_2 |  | UDINT |  | HoldingRegister | 868
4632 | MB_FanSupply_Adr_3 |  | UDINT |  | HoldingRegister | 870
4631 | MB_FanSupply_Adr_4 |  | UDINT |  | HoldingRegister | 872
4630 | MB_FanSupply_Adr_5 |  | UDINT |  | HoldingRegister | 874
4629 | MB_FanSupply_Adr_6 |  | UDINT |  | HoldingRegister | 876
4628 | MB_FanSupply_Adr_7 |  | UDINT |  | HoldingRegister | 878
4627 | MB_FanSupply_Adr_8 |  | UDINT |  | HoldingRegister | 880
4626 | MB_FanSupply_Adr_9 |  | UDINT |  | HoldingRegister | 882
4625 | MB_FanSupply_Adr_10 |  | UDINT |  | HoldingRegister | 884
4624 | MB_FanReturn_Adr_1 |  | UDINT |  | HoldingRegister | 886
4623 | MB_FanReturn_Adr_2 |  | UDINT |  | HoldingRegister | 888
4622 | MB_FanReturn_Adr_3 |  | UDINT |  | HoldingRegister | 890
4621 | MB_FanReturn_Adr_4 |  | UDINT |  | HoldingRegister | 892
4620 | MB_FanReturn_Adr_5 |  | UDINT |  | HoldingRegister | 894
4619 | MB_FanReturn_Adr_6 |  | UDINT |  | HoldingRegister | 896
4618 | MB_FanReturn_Adr_7 |  | UDINT |  | HoldingRegister | 898
4617 | MB_FanReturn_Adr_8 |  | UDINT |  | HoldingRegister | 900
4616 | MB_FanReturn_Adr_9 |  | UDINT |  | HoldingRegister | 902
4615 | MB_FanReturn_Adr_10 |  | UDINT |  | HoldingRegister | 904
4614 | MB_Devices.VFD_1.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 906
4613 | MB_Devices.VFD_2.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 907
4612 | MB_Devices.VFD_3.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 908
4611 | MB_Devices.VFD_4.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 909
4610 | MB_Devices.VFD_5.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 910
4609 | MB_Devices.VFD_6.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 911
4608 | MB_Devices.VFD_7.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 912
4607 | MB_Devices.VFD_8.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 913
4606 | MB_Devices.VFD_9.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 914
4605 | MB_Devices.VFD_10.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 915
4604 | MB_Devices.VFD_11.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 916
4603 | MB_Devices.VFD_12.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 917
4602 | MB_Devices.VFD_13.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 918
4601 | MB_Devices.VFD_14.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 919
4600 | MB_Devices.VFD_15.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 920
4599 | MB_Devices.VFD_16.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 921
4598 | MB_Devices.VFD_17.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 922
4597 | MB_Devices.VFD_18.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 923
4596 | MB_Devices.VFD_19.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 924
4595 | MB_Devices.VFD_20.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 925
4594 | MB_Devices.VFD_21.MBM_Params.MaxFreq |  | INT |  | HoldingRegister | 926
4593 | UnitSetP_AirFlwSetP_StandBy |  | UREAL16 |  | HoldingRegister | 927
4592 | UnitSetP_AirFlwSetP_StandBy_2 |  | UREAL16 |  | HoldingRegister | 928
4591 | MB_Set_Test |  | UINT |  | HoldingRegister | 929
4590 | MB_Set_IRMS_Read |  | INT |  | HoldingRegister | 930
4589 | MB_Set_FW_Read |  | INT |  | HoldingRegister | 931
4588 | MB_Set_Error_Read |  | INT |  | HoldingRegister | 932
4587 | MB_Set_Direct_Read |  | INT |  | HoldingRegister | 933
4586 | MB_Set_Detect_Read |  | INT |  | HoldingRegister | 934
4585 | MB_Set_Detect |  | INT |  | HoldingRegister | 935
4584 | MB_Set_Addr |  | INT |  | HoldingRegister | 936
4583 | MB_Set_Addr_New |  | INT |  | HoldingRegister | 937
4582 | MB_Set_Addr_Read |  | INT |  | HoldingRegister | 938
4581 | MB_Set_Addr_Old |  | INT |  | HoldingRegister | 939
4580 | MB_Set_Case |  | UINT |  | HoldingRegister | 940
4579 | MB_Set_MaxRPM |  | INT |  | HoldingRegister | 941
4578 | MB_Set_MaxRPM_Read |  | INT |  | HoldingRegister | 942
4577 | MB_Set_MinRPM_Read |  | INT |  | HoldingRegister | 943
4576 | MB_Set_Mode |  | INT |  | HoldingRegister | 944
4575 | MB_Set_Mode_Read |  | INT |  | HoldingRegister | 945
4574 | MB_Set_Password |  | INT |  | HoldingRegister | 946
4573 | MB_Set_Power_Read |  | INT |  | HoldingRegister | 947
4572 | MB_Set_Speed_Read |  | INT |  | HoldingRegister | 948
4571 | N_Alarm |  | INT |  | HoldingRegister | 949
4570 | Scheduler_OnOffUnit.Scheduler_1.DaysSchedMsg |  | UINT |  | HoldingRegister | 950
4569 | Scheduler_OnOffUnit.Scheduler_1.VacationsMsg |  | UINT |  | HoldingRegister | 951
4568 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysMsg |  | UINT |  | HoldingRegister | 952
4567 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SH_Val | Superheat | UREAL16 |  | HoldingRegister | 953 | K | Heat Pump cPCO variable
4566 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_rps | Current rotor speed [rps] | UREAL16 |  | HoldingRegister | 955
4565 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_EEV_Pos%_Val | Valve opening | UREAL16 |  | HoldingRegister | 957 | % | Heat Pump cPCO variable
4564 | PWRP_Info_MotA |  | UREAL16 |  | HoldingRegister | 959
4563 | UnitStatus |  | UINT |  | HoldingRegister | 960
4562 | CompPwrReq |  | REAL |  | HoldingRegister | 961
4561 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_Perc | Current rotor speed [%] | REAL |  | HoldingRegister | 963 | %
4560 | DscgP |  | REAL |  | HoldingRegister | 965
4559 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CondTemp_Val | Condensing temperature | REAL |  | HoldingRegister | 967 | °C | Heat Pump cPCO variable
4558 | DscgTemp |  | REAL |  | HoldingRegister | 969
4557 | SuctTemp |  | REAL |  | HoldingRegister | 971
4556 | SuctP |  | REAL |  | HoldingRegister | 973
4555 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SH_EvapTemp_Val | Evaporation temperature | REAL |  | HoldingRegister | 975 | °C | Heat Pump cPCO variable
4554 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val | Valve position | UINT |  | HoldingRegister | 977 |  | Heat Pump cPCO variable
4553 | EEVSet |  | REAL |  | HoldingRegister | 978
4552 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_DscgSH_Val | Discharge superheat | REAL |  | HoldingRegister | 980 | K | Heat Pump cPCO variable
4551 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_DriveStatus | Drive status | INT |  | HoldingRegister | 982
4550 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotA | Current motor current [A] | REAL |  | HoldingRegister | 983 | A
4549 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotV | Current motor voltage [V] | UINT |  | HoldingRegister | 985 | V
4548 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotPwr | Current motor consumption [W] | REAL |  | HoldingRegister | 986
4547 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR113_DCBusVoltage | DC bus voltage | UINT |  | HoldingRegister | 988
4546 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR134_DCBusRipple | DC bus ripple | UINT |  | HoldingRegister | 989
4545 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_DriveTemp | Drive temperature | REAL |  | HoldingRegister | 990 | °C
4544 | AHU_ID_Char[0] |  | INT |  | HoldingRegister | 992 |  | ASCII
4543 | AHU_ID_Char[1] |  | INT |  | HoldingRegister | 993 |  | ASCII
4542 | AHU_ID_Char[2] |  | INT |  | HoldingRegister | 994 |  | ASCII
4541 | AHU_ID_Char[3] |  | INT |  | HoldingRegister | 995 |  | ASCII
4540 | AHU_ID_Char[4] |  | INT |  | HoldingRegister | 996 |  | ASCII
4539 | AHU_ID_Char[5] |  | INT |  | HoldingRegister | 997 |  | ASCII
4538 | AHU_ID_Char[6] |  | INT |  | HoldingRegister | 998 |  | ASCII
4537 | AHU_ID_Char[7] |  | INT |  | HoldingRegister | 999 |  | ASCII
4536 | AHU_ID_Char[8] |  | INT |  | HoldingRegister | 1000 |  | ASCII
4535 | AHU_ID_Char[9] |  | INT |  | HoldingRegister | 1001 |  | ASCII
4534 | AHU_ID_Char[10] |  | INT |  | HoldingRegister | 1002 |  | ASCII
4533 | AHU_ID_Char[11] |  | INT |  | HoldingRegister | 1003 |  | ASCII
4532 | AHU_ID_Char[12] |  | INT |  | HoldingRegister | 1004 |  | ASCII
4531 | AHU_ID_Char[13] |  | INT |  | HoldingRegister | 1005 |  | ASCII
4530 | AHU_ID_Char[14] |  | INT |  | HoldingRegister | 1006 |  | ASCII
4529 | AHU_ID_Char[15] |  | INT |  | HoldingRegister | 1007 |  | ASCII
4528 | AHU_ID_Char[16] |  | INT |  | HoldingRegister | 1008 |  | ASCII
4527 | AHU_ID_Char[17] |  | INT |  | HoldingRegister | 1009 |  | ASCII
4526 | AHU_ID_Char[18] |  | INT |  | HoldingRegister | 1010 |  | ASCII
4525 | AHU_ID_Char[19] |  | INT |  | HoldingRegister | 1011 |  | ASCII
4524 | AL_ActiveAlarmsQuantity |  | DINT |  | HoldingRegister | 1012
4523 | AL_ActiveAlarmsPointer |  | DINT |  | HoldingRegister | 1014
4522 | AL_ActiveAlarmsPointerSent |  | DINT |  | HoldingRegister | 1016
4521 | AL_ActiveAlarmsNumberSent |  | DINT |  | HoldingRegister | 1018
4520 | AL_ActiveAlarmsTimeStampSent |  | DINT |  | HoldingRegister | 1020
4519 | AL_LogAlarmsPointer |  | DINT |  | HoldingRegister | 1022
4518 | AL_LogAlarmsPointerSent |  | DINT |  | HoldingRegister | 1024
4517 | AL_LogAlarmsNumberSent |  | DINT |  | HoldingRegister | 1026
4516 | AL_LogAlarmsTypeSent |  | UINT |  | HoldingRegister | 1028
4515 | AL_LogAlarmsTimeStampSent |  | DINT |  | HoldingRegister | 1029
4514 | En_ReadFromFile |  | UINT |  | HoldingRegister | 1031
2432 | En_ReadFromFile |  | UInt |  | HoldingRegister | 2021
2433 | AppCode_Rec | SYS - Application Code - Recirculation - XX - _ . _ . _ . _ . _ . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2022 |  | 0 - AS:Supply 1 - AD: S+E 2 - AR: S/E & Rotary 3 - AP: S/E + Cross 4 - AG: S/E + Glycol 5 - AX: S/E+HeatPump 6 - AE: Exhaust
2434 | AppCode_Heat | SYS - Application Code - Heating - _ _ - X . _ . _ . _ . _ . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2023 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater 4 - Steam
2435 | AppCode_Cool | SYS - Application Code - Cooling - _ _ - _ . X . _ . _ . _ . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2024 |  | 0 - None 1 - Chilled water 2 - DX
2436 | AppCode_Rev | SYS - Application Code - Rev - _ _ - _ . _ . X . _ . _ . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2025 |  | 0 - None 1 - Hydronic 2 - DX
2437 | AppCode_PreHeat | SYS - Application Code - PreHeating - _ _ - _ . _ . _ . X . _ . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2026 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater
2438 | AppCode_ReHeat | SYS - Application Code - Recirculation Heating - _ _ - _ . _ . _ . _ . X . _ . _ . _ | USInt | ReadWrite | HoldingRegister | 2027 |  | 0 - None 1 - Hot water 2 - DX 3 - Electric heater
2439 | AppCode_Eco | SYS - Application Code - ECO - _ _ - _ . _ . _ . _ . _ . X . _ . _ | USInt | ReadWrite | HoldingRegister | 2028 |  | 0 - NO 1 - YES
2440 | AppCode_Hum | SYS - Application Code - Humidity - _ _ - _ . _ . _ . _ . _ . _ . X . _ | USInt | ReadWrite | HoldingRegister | 2029 |  | 0 - None 1 - Evaporative 2 - Steam
2441 | AppCode_Board | SYS - Application Code - Board - _ _ - _ . _ . _ . _ . _ . _ . _ . X | USInt | ReadWrite | HoldingRegister | 2030 |  | 0 - uPC3 XS 1 - uPC3 XS 2 - uPC3 Small 3 - uPC3 XS 4 - uPC3 XS 5 - uPC3 XS 6 - uPC3 XS
2446 | DayIn | CLK - Time - Setting - Day | UInt | ReadWrite | HoldingRegister | 2035 |  | 44957
2447 | GeneralMng.Zone_TZ | CLK - Time - Setting - Zone | UInt | ReadWrite | HoldingRegister | 2036
2448 | HourIn | CLK - Time - Setting - Hour [h] | UInt | ReadWrite | HoldingRegister | 2037 | h
2449 | MinuteIn | CLK - Time - Setting - Minute [min.] | UInt | ReadWrite | HoldingRegister | 2038 | min.
2450 | MonthIn | CLK - Time - Setting - Month | UInt | ReadWrite | HoldingRegister | 2039 |  | 44938
2451 | SecondIn | CLK - Time - Setting - Second [sec.] | UInt | ReadWrite | HoldingRegister | 2040 | sec.
2452 | YearIn | CLK - Time - Setting - Year | UInt | ReadWrite | HoldingRegister | 2041 |  | 0 - 99
2453 | Day | CLK - Time - Day | UInt | Read | HoldingRegister | 2042 |  | 44957
2454 | DayOfWeek | CLK - Time - Setting - Day of Week | UInt | Read | HoldingRegister | 2043 |  | 1 - MON 2 - TUE 3 - WED 4 - THU 5 - FRI 6 - SAT 7 - SUN
2455 | Hour | CLK - Time - Hour [h] | UInt | Read | HoldingRegister | 2044 | h
2456 | Minute | CLK - Time - Minute [min.] | UInt | Read | HoldingRegister | 2045 | min.
2457 | Month | CLK - Time - Month | UInt | Read | HoldingRegister | 2046 |  | 44938
2458 | Second | CLK - Time - Second [sec.] | UInt | Read | HoldingRegister | 2047 | sec.
2459 | Year | CLK - Time - Year | UInt | Read | HoldingRegister | 2048 |  | 0 - 99
2460 | AfterPreHeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - After PreHeat [°C] | USInt | ReadWrite | HoldingRegister | 2049 | °C | 0 - AUTO OR 1 - 100%
2461 | AfterPreHeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - After PreHeat [°C] | Real | ReadWrite | HoldingRegister | 2050 | °C
2462 | AppHumReg | SYS - Unit Configuration - Humidity Regulation | USInt | ReadWrite | HoldingRegister | 2052 |  | 0 - NONE 1 - SUPPLY 2 - RETURN 3 - ROOM
2463 | AppTempReg | SYS - Unit Configuration - Temperature Regulation | USInt | ReadWrite | HoldingRegister | 2053 |  | 0 - SUPPLY 1 - RETURN 2 - ROOM
2464 | BMS_Addr | SYS - Unit Configuration - BMS port - Address | USInt | ReadWrite | HoldingRegister | 2054 |  | 11689
2465 | CO2_Simulation_Var | SYS - IO Setting - CO2 Simulate - Value [ppm] | Int | ReadWrite | HoldingRegister | 2055 | ppm
2466 | CoolAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Cool | USInt | ReadWrite | HoldingRegister | 2056 |  | 0 - AUTO 1 - OFF 2 - ON
2467 | DriveTyp | SYS - Unit Configuration - Import / Export - Memory Type | Byte | ReadWrite | HoldingRegister | 2057 |  | 0 - FLASH MEMORY 1 - USB
2468 | ExhFanRegTyp | SYS - Unit Configuration - Regulation Return | USInt | ReadWrite | HoldingRegister | 2058 |  | 0 - NONE 1 - VAV 2 - CAV
2469 | ExhMulti | SYS - Unit Configuration - Config Return | USInt | ReadWrite | HoldingRegister | 2059 |  | 0 - 1 FAN 1 - REDUNDANT 2 - 2 FANS 3 - 3 FANS 4 - 4 FANS 5 - 5 FANS 6 - 6 FANS 7 - 7 FANS 8 - 8 FANS 9 - 9 FANS 10 - 10 FANS
2470 | ExhTemp.Man | SYS - IO Setting - Manual - Temperature Exhaust [°C] | USInt | ReadWrite | HoldingRegister | 2060 | °C | 0 - AUTO OR 1 - 100%
2471 | ExhTemp.Offset | SYS - IO Setting - Offset - Temperature Exhaust [°C] | Real | ReadWrite | HoldingRegister | 2061 | °C
2472 | ExtTemp.Man | SYS - IO Setting - Manual - Temperature - External [°C] | USInt | ReadWrite | HoldingRegister | 2063 | °C | 0 - AUTO OR 1 - 100%
2473 | ExtTemp.Offset | SYS - IO Setting - Offset - Temperature - External [°C] | Real | ReadWrite | HoldingRegister | 2064 | °C
2474 | FB_Baud_msk | SYS - Unit Configuration - FieldBus Port - Baudrate | Int | ReadWrite | HoldingRegister | 2066 |  | 0 - 4800 1 - 9600 2 - 19200 3 - 38400
2475 | FireAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm Fire | USInt | ReadWrite | HoldingRegister | 2067 |  | 0 - AUTO 1 - OFF 2 - ON
2476 | HumAlrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Humidifier | USInt | ReadWrite | HoldingRegister | 2068 |  | 0 - AUTO 1 - OFF 2 - ON
2477 | ID2_Alrm.Man | SYS - IO Setting - Digital Input - Manual - Alarm - Heat | USInt | ReadWrite | HoldingRegister | 2069 |  | 0 - AUTO 1 - OFF 2 - ON
2478 | ImpExpFileName | SYS - Unit Configuration - Import / Export - File Name | Int | ReadWrite | HoldingRegister | 2070 |  | 0 - 99
2479 | LangChange | SYS - Unit Configuration - Language | DInt | ReadWrite | HoldingRegister | 2071 |  | 0 - EN 1 - PL
2480 | MinFanPwrRet | SYS - Unit Configuration - Minimum Speed - Return [%] | Real | ReadWrite | HoldingRegister | 2073 | % | 0 - 100 %
2481 | MinFanPwrSup | SYS - Unit Configuration - Minimum Speed - Supply [%] | Real | ReadWrite | HoldingRegister | 2075 | % | 0 - 100 %
2482 | OffTotMinutes | SYS - Hardware - Time last blackout [min.] | UInt | ReadWrite | HoldingRegister | 2077 | min.
2483 | OnOffStatus | SYS - Hardware - Machine Status [msec.] | USInt | ReadWrite | HoldingRegister | 2078 | msec.
2484 | PrgCycleMs | SYS - Hardware - Cycle [msec.] | UInt | ReadWrite | HoldingRegister | 2079 | msec.
2485 | RecSupplyTemp.Man | SYS - IO Setting - Manual - Temperature - Supply Recovery [°C] | USInt | ReadWrite | HoldingRegister | 2080 | °C | 0 - AUTO OR 1 - 100%
2486 | RecSupplyTemp.Offset | SYS - IO Setting - Offset - Temperature - Supply Recovery [°C] | Real | ReadWrite | HoldingRegister | 2081 | °C
2487 | RemoteOn.Man | SYS - IO Setting - Digital Input - Manual - Remote ON | USInt | ReadWrite | HoldingRegister | 2083 |  | 0 - AUTO 1 - OFF 2 - ON
2488 | RetFilter.Man | SYS - IO Setting - Digital Input - Manual - Filter - Return | USInt | ReadWrite | HoldingRegister | 2084 |  | 0 - AUTO 1 - OFF 2 - ON
2489 | RetTemp.Man | SYS - IO Setting - Manual - Temperature - Return [°C] | USInt | ReadWrite | HoldingRegister | 2085 | °C | 0 - AUTO OR 1 - 100%
2490 | RetTemp.Offset | SYS - IO Setting - Offset - Temperature - Return [°C] | Real | ReadWrite | HoldingRegister | 2086 | °C
2491 | SupplyFanRegTyp | SYS - Unit Configuration - Regulation Supply | USInt | ReadWrite | HoldingRegister | 2088 |  | 0 - NONE 1 - VAV 2 - CAV
2492 | SupplyFilter.Man | SYS - IO Setting - Digital Input - Manual - Filter - Supply | USInt | ReadWrite | HoldingRegister | 2089 |  | 0 - AUTO 1 - OFF 2 - ON
2493 | SupplyMulti | SYS - Unit Configuration - Config Supply | USInt | ReadWrite | HoldingRegister | 2090 |  | 0 - 1 FAN 1 - REDUNDANT 2 - 2 FANS 3 - 3 FANS 4 - 4 FANS 5 - 5 FANS 6 - 6 FANS 7 - 7 FANS 8 - 8 FANS 9 - 9 FANS 10 - 10 FANS
2494 | SupplyTemp.Man | SYS - IO Setting - Manual - Temperature - Supply [°C] | USInt | ReadWrite | HoldingRegister | 2091 | °C | 0 - AUTO OR 1 - 100%
2495 | SupplyTemp.Offset | SYS - IO Setting - Offset - Temperature - Supply [°C] | Real | ReadWrite | HoldingRegister | 2092 | °C
2496 | Typ_SP_CO2 | SYS - IO Setting - Modbus Probe Type - CO2 | USInt | ReadWrite | HoldingRegister | 2094 |  | 0 - TYPE 1 1 - TYPE 2
2497 | Typ_SP_Hum | SYS - IO Setting - Modbus Probe Type - Humidity | USInt | ReadWrite | HoldingRegister | 2095 |  | 0 - TYPE 1 1 - TYPE 2
2498 | Typ_SP_Pressure | SYS - IO Setting - Modbus Probe Type - Pressure | USInt | ReadWrite | HoldingRegister | 2096 |  | 0 - TYPE 1 1 - TYPE 2
2499 | TypVFD | SYS - Unit Configuration - Supply Fan VFD Type | USInt | ReadWrite | HoldingRegister | 2097 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2500 | TypVFD_2 | SYS - Unit Configuration - Return Fan VFD Type | USInt | ReadWrite | HoldingRegister | 2098 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2501 | TypVFD_Rotor | SYS - Unit Configuration - Rotor Fan VFD Type | USInt | ReadWrite | HoldingRegister | 2099 |  | 0 - iC5 1 - iG5 2 - ABB 3 - EC 4 - DFI 5 - M100 6 - None
2502 | Uom_Msk | SYS - Unit Configuration - Unit of Measure | DInt | ReadWrite | HoldingRegister | 2100 |  | 1 - INTERNATIONAL 2 - USA
2503 | W_HeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - Water Heat [°C] | USInt | ReadWrite | HoldingRegister | 2102 | °C | 0 - AUTO OR 1 - 100%
2504 | W_HeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - Water Heat [°C] | Real | ReadWrite | HoldingRegister | 2103 | °C
2505 | W_PreHeatCoilTemp.Man | SYS - IO Setting - Manual - Temperature - Water PreHeat [°C] | USInt | ReadWrite | HoldingRegister | 2105 | °C | 0 - AUTO OR 1 - 100%
2506 | W_PreHeatCoilTemp.Offset | SYS - IO Setting - Offset - Temperature - Water PreHeat [°C] | Real | ReadWrite | HoldingRegister | 2106 | °C
2507 | WinSum.Man | SYS - IO Setting - Digital Input - Manual - Winter / Summer | USInt | ReadWrite | HoldingRegister | 2108 |  | 0 - AUTO 1 - OFF 2 - ON
3474 | ErrParamImpExp |  | Dint |  | HoldingRegister | 2109
2508 | Scheduler_OnOffUnit.Scheduler_1.VacationsDailyChk.CurrentWkDay |  | UInt |  | HoldingRegister | 2151
2509 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Hours | SCH - Scheduller - Monday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2152 | h | 00-23
2510 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].Mins | SCH - Scheduller - Monday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2153 | min. | 0 - 59
2511 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[0].UnitStatus | SCH - Scheduller - Monday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2154 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2512 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Hours | SCH - Scheduller - Monday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2155 | h | 0 - 23
2513 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].Mins | SCH - Scheduller - Monday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2156 | min. | 0 - 59
2514 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[1].UnitStatus | SCH - Scheduller - Monday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2157 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2515 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Hours | SCH - Scheduller - Monday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2158 | h | 0 - 23
2516 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].Mins | SCH - Scheduller - Monday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2159 | min. | 0 - 59
2517 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[2].UnitStatus | SCH - Scheduller - Monday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2160 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2518 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Hours | SCH - Scheduller - Monday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2161 | h | 0 - 23
2519 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].Mins | SCH - Scheduller - Monday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2162 | min. | 0 - 59
2520 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[0].EVENT[3].UnitStatus | SCH - Scheduller - Monday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2163 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2521 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Hours | SCH - Scheduller - Tuesday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2164 | h | 0 - 23
2522 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].Mins | SCH - Scheduller - Tuesday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2165 | min. | 0 - 59
2523 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[0].UnitStatus | SCH - Scheduller - Tuesday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2166 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2524 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Hours | SCH - Scheduller - Tuesday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2167 | h | 0 - 23
2525 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].Mins | SCH - Scheduller - Tuesday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2168 | min. | 0 - 59
2526 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[1].UnitStatus | SCH - Scheduller - Tuesday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2169 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2527 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Hours | SCH - Scheduller - Tuesday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2170 | h | 0 - 23
2528 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].Mins | SCH - Scheduller - Tuesday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2171 | min. | 0 - 59
2529 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[2].UnitStatus | SCH - Scheduller - Tuesday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2172 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2530 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Hours | SCH - Scheduller - Tuesday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2173 | h | 0 - 23
2531 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].Mins | SCH - Scheduller - Tuesday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2174 | min. | 0 - 59
2532 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[1].EVENT[3].UnitStatus | SCH - Scheduller - Tuesday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2175 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2533 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Hours | SCH - Scheduller - Wednesday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2176 | h | 0 - 23
2534 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].Mins | SCH - Scheduller - Wednesday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2177 | min. | 0 - 59
2535 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[0].UnitStatus | SCH - Scheduller - Wednesday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2178 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2536 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Hours | SCH - Scheduller - Wednesday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2179 | h | 0 - 23
2537 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].Mins | SCH - Scheduller - Wednesday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2180 | min. | 0 - 59
2538 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[1].UnitStatus | SCH - Scheduller - Wednesday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2181 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2539 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Hours | SCH - Scheduller - Wednesday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2182 | h | 0 - 23
2540 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].Mins | SCH - Scheduller - Wednesday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2183 | min. | 0 - 59
2541 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[2].UnitStatus | SCH - Scheduller - Wednesday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2184 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2542 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Hours | SCH - Scheduller - Wednesday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2185 | h | 0 - 23
2543 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].Mins | SCH - Scheduller - Wednesday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2186 | min. | 0 - 59
2544 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[2].EVENT[3].UnitStatus | SCH - Scheduller - Wednesday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2187 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2545 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Hours | SCH - Scheduller - Thursday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2188 | h | 0 - 23
2546 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].Mins | SCH - Scheduller - Thursday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2189 | min. | 0 - 59
2547 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[0].UnitStatus | SCH - Scheduller - Thursday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2190 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2548 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Hours | SCH - Scheduller - Thursday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2191 | h | 0 - 23
2549 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].Mins | SCH - Scheduller - Thursday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2192 | min. | 0 - 59
2550 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[1].UnitStatus | SCH - Scheduller - Thursday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2193 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2551 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Hours | SCH - Scheduller - Thursday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2194 | h | 0 - 23
2552 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].Mins | SCH - Scheduller - Thursday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2195 | min. | 0 - 59
2553 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[2].UnitStatus | SCH - Scheduller - Thursday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2196 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2554 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Hours | SCH - Scheduller - Thursday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2197 | h | 0 - 23
2555 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].Mins | SCH - Scheduller - Thursday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2198 | min. | 0 - 59
2556 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[3].EVENT[3].UnitStatus | SCH - Scheduller - Thursday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2199 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2557 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Hours | SCH - Scheduller - Friday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2200 | h | 0 - 23
2558 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].Mins | SCH - Scheduller - Friday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2201 | min. | 0 - 59
2559 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[0].UnitStatus | SCH - Scheduller - Friday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2202 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2560 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Hours | SCH - Scheduller - Friday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2203 | h | 0 - 23
2561 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].Mins | SCH - Scheduller - Friday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2204 | min. | 0 - 59
2562 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[1].UnitStatus | SCH - Scheduller - Friday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2205 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2563 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Hours | SCH - Scheduller - Friday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2206 | h | 0 - 23
2564 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].Mins | SCH - Scheduller - Friday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2207 | min. | 0 - 59
2565 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[2].UnitStatus | SCH - Scheduller - Friday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2208 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2566 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Hours | SCH - Scheduller - Friday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2209 | h | 0 - 23
2567 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].Mins | SCH - Scheduller - Friday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2210 | min. | 0 - 59
2568 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[4].EVENT[3].UnitStatus | SCH - Scheduller - Friday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2211 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2569 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Hours | SCH - Scheduller - Saturday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2212 | h | 0 - 23
2570 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].Mins | SCH - Scheduller - Saturday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2213 | min. | 0 - 59
2571 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[0].UnitStatus | SCH - Scheduller - Saturday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2214 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2572 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Hours | SCH - Scheduller - Saturday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2215 | h | 0 - 23
2573 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].Mins | SCH - Scheduller - Saturday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2216 | min. | 0 - 59
2574 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[1].UnitStatus | SCH - Scheduller - Saturday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2217 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2575 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Hours | SCH - Scheduller - Saturday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2218 | h | 0 - 23
2576 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].Mins | SCH - Scheduller - Saturday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2219 | min. | 0 - 59
2577 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[2].UnitStatus | SCH - Scheduller - Saturday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2220 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2578 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Hours | SCH - Scheduller - Saturday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2221 | h | 0 - 23
2579 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].Mins | SCH - Scheduller - Saturday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2222 | min. | 0 - 59
2580 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[5].EVENT[3].UnitStatus | SCH - Scheduller - Saturday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2223 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2581 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Hours | SCH - Scheduller - Sunday - 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2224 | h | 0 - 23
2582 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].Mins | SCH - Scheduller - Sunday - 1 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2225 | min. | 0 - 59
2583 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[0].UnitStatus | SCH - Scheduller - Sunday - 1 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2226 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2584 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Hours | SCH - Scheduller - Sunday - 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2227 | h | 0 - 23
2585 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].Mins | SCH - Scheduller - Sunday - 2 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2228 | min. | 0 - 59
2586 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[1].UnitStatus | SCH - Scheduller - Sunday - 2 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2229 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2587 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Hours | SCH - Scheduller - Sunday - 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2230 | h | 0 - 23
2588 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].Mins | SCH - Scheduller - Sunday - 3 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2231 | min. | 0 - 59
2589 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[2].UnitStatus | SCH - Scheduller - Sunday - 3 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2232 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2590 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Hours | SCH - Scheduller - Sunday - 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2233 | h | 0 - 23
2591 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].Mins | SCH - Scheduller - Sunday - 4 - Mins [min.] | USInt | ReadWrite | HoldingRegister | 2234 | min. | 0 - 59
2592 | Scheduler_OnOffUnit.Scheduler_1.DaysSched[6].EVENT[3].UnitStatus | SCH - Scheduller - Sunday - 4 - UnitStatus | USInt | ReadWrite | HoldingRegister | 2235 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2593 | Scheduler_OnOffUnit.Scheduler_1.EnDayCopy | SCH - Scheduller - Time Band - Enable Copy to Day | USInt | ReadWrite | HoldingRegister | 2236 |  | 0 - NO 1 - YES
2594 | Scheduler_OnOffUnit.Scheduler_1.SaveData | SCH - Scheduller - Time Band - Save Data | USInt | ReadWrite | HoldingRegister | 2237 |  | 0 - NO 1 - YES
2595 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].SpecialDay | SCH - Scheduller - Special Days 1 - Day | USInt | ReadWrite | HoldingRegister | 2238 |  | 44957
2596 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].SpecialMonth | SCH - Scheduller - Special Days 1 - Month | USInt | ReadWrite | HoldingRegister | 2239 |  | 44938
2597 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[0].UnitStatus | SCH - Scheduller - Special Days 1 - Unit Status | USInt | ReadWrite | HoldingRegister | 2240 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2598 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].SpecialDay | SCH - Scheduller - Special Days 2 - Day | USInt | ReadWrite | HoldingRegister | 2241 |  | 44957
2599 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].SpecialMonth | SCH - Scheduller - Special Days 2 - Month | USInt | ReadWrite | HoldingRegister | 2242 |  | 44938
2600 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[1].UnitStatus | SCH - Scheduller - Special Days 2 - Unit Status | USInt | ReadWrite | HoldingRegister | 2243 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2601 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].SpecialDay | SCH - Scheduller - Special Days 3 - Day | USInt | ReadWrite | HoldingRegister | 2244 |  | 44957
2602 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].SpecialMonth | SCH - Scheduller - Special Days 3 - Month | USInt | ReadWrite | HoldingRegister | 2245 |  | 44938
2603 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[2].UnitStatus | SCH - Scheduller - Special Days 3 - Unit Status | USInt | ReadWrite | HoldingRegister | 2246 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2604 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].SpecialDay | SCH - Scheduller - Special Days 4 - Day | USInt | ReadWrite | HoldingRegister | 2247 |  | 44957
2605 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].SpecialMonth | SCH - Scheduller - Special Days 4 - Month | USInt | ReadWrite | HoldingRegister | 2248 |  | 44938
2606 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[3].UnitStatus | SCH - Scheduller - Special Days 4 - Unit Status | USInt | ReadWrite | HoldingRegister | 2249 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2607 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].SpecialDay | SCH - Scheduller - Special Days 5 - Day | USInt | ReadWrite | HoldingRegister | 2250 |  | 44957
2608 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].SpecialMonth | SCH - Scheduller - Special Days 5 - Month | USInt | ReadWrite | HoldingRegister | 2251 |  | 44938
2609 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[4].UnitStatus | SCH - Scheduller - Special Days 5 - Unit Status | USInt | ReadWrite | HoldingRegister | 2252 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2610 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].SpecialDay | SCH - Scheduller - Special Days 6 - Day | USInt | ReadWrite | HoldingRegister | 2253 |  | 44957
2611 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].SpecialMonth | SCH - Scheduller - Special Days 6 - Month | USInt | ReadWrite | HoldingRegister | 2254 |  | 44938
2612 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysSched[5].UnitStatus | SCH - Scheduller - Special Days 6 - Unit Status | USInt | ReadWrite | HoldingRegister | 2255 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2613 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Hours | SCH - Scheduller - Time Band 1 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2256 | h | 0 - 23
2614 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].Mins | SCH - Scheduller - Time Band 1 - Minute [min.] | USInt | ReadWrite | HoldingRegister | 2257 | min. | 0 - 59
2615 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[0].UnitStatus | SCH - Scheduller - Time Band 1 - Unit Status | USInt | ReadWrite | HoldingRegister | 2258 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2616 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Hours | SCH - Scheduller - Time Band 2 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2259 | h | 0 - 23
2617 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].Mins | SCH - Scheduller - Time Band 2 - Minute [min.] | USInt | ReadWrite | HoldingRegister | 2260 | min. | 0 - 59
2618 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[1].UnitStatus | SCH - Scheduller - Time Band 2 - Unit Status | USInt | ReadWrite | HoldingRegister | 2261 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2619 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Hours | SCH - Scheduller - Time Band 3 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2262 | h | 0 - 23
2620 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].Mins | SCH - Scheduller - Time Band 3 - Minute [min.] | USInt | ReadWrite | HoldingRegister | 2263 | min. | 0 - 59
2621 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[2].UnitStatus | SCH - Scheduller - Time Band 3 - Unit Status | USInt | ReadWrite | HoldingRegister | 2264 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2622 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Hours | SCH - Scheduller - Time Band 4 - Hours [h] | USInt | ReadWrite | HoldingRegister | 2265 | h | 0 - 23
2623 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].Mins | SCH - Scheduller - Time Band 4 - Minute [min.] | USInt | ReadWrite | HoldingRegister | 2266 | min. | 0 - 59
2624 | Scheduler_OnOffUnit.Scheduler_1.Event_Msk[3].UnitStatus | SCH - Scheduller - Time Band 4 - Unit Status | USInt | ReadWrite | HoldingRegister | 2267 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2625 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].EndDay | SCH - Scheduller - Periods 1 - End Day | USInt | ReadWrite | HoldingRegister | 2268 |  | 44957
2626 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].EndMonth | SCH - Scheduller - Periods 1 - End Month | USInt | ReadWrite | HoldingRegister | 2269 |  | 44938
2627 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].StartDay | SCH - Scheduller - Periods 1 - Start Day | USInt | ReadWrite | HoldingRegister | 2270 |  | 44957
2628 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].StartMonth | SCH - Scheduller - Periods 1 - Start Month | USInt | ReadWrite | HoldingRegister | 2271 |  | 44938
2629 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[0].UnitStatus | SCH - Scheduller - Periods 1 - Unit Status | USInt | ReadWrite | HoldingRegister | 2272 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2630 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].EndDay | SCH - Scheduller - Periods 2 - End Day | USInt | ReadWrite | HoldingRegister | 2273 |  | 44957
2631 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].EndMonth | SCH - Scheduller - Periods 2 - End Month | USInt | ReadWrite | HoldingRegister | 2274 |  | 44938
2632 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].StartDay | SCH - Scheduller - Periods 2 - Start Day | USInt | ReadWrite | HoldingRegister | 2275 |  | 44957
2633 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].StartMonth | SCH - Scheduller - Periods 2 - Start Month | USInt | ReadWrite | HoldingRegister | 2276 |  | 44938
2634 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[1].UnitStatus | SCH - Scheduller - Periods 2 - Unit Status | USInt | ReadWrite | HoldingRegister | 2277 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2635 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].EndDay | SCH - Scheduller - Periods 3 - End Day | USInt | ReadWrite | HoldingRegister | 2278 |  | 44957
2636 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].EndMonth | SCH - Scheduller - Periods 3 - End Month | USInt | ReadWrite | HoldingRegister | 2279 |  | 44938
2637 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].StartDay | SCH - Scheduller - Periods 3 - Start Day | USInt | ReadWrite | HoldingRegister | 2280 |  | 44957
2638 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].StartMonth | SCH - Scheduller - Periods 3 - Start Month | USInt | ReadWrite | HoldingRegister | 2281 |  | 44938
2639 | Scheduler_OnOffUnit.Scheduler_1.VacationsSched[2].UnitStatus | SCH - Scheduller - Periods 3 - Unit Status | USInt | ReadWrite | HoldingRegister | 2282 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY
2640 | SetTypSched | SP - WorkMode - Actual | USInt | Read | HoldingRegister | 2283
2641 | TypScheduler | SCH - Scheduller - Type | USInt | ReadWrite | HoldingRegister | 2284 |  | 0 - NONE 1 - BOARD 2 - HMI
2642 | CurrUnitStatus | SCH - Scheduller - Actual mode from scheduller | USInt | Read | HoldingRegister | 2285 |  | 0 - OFF 1 - ECO 2 - Optimal 3 - Comfort
2643 | Scheduler_OnOffUnit.Scheduler_1.DaysSchedMsg |  | USInt |  | HoldingRegister | 2286
2644 | Scheduler_OnOffUnit.Scheduler_1.VacationsMsg |  | USInt |  | HoldingRegister | 2287
2645 | Scheduler_OnOffUnit.Scheduler_1.SpecDaysMsg |  | USInt |  | HoldingRegister | 2288
2646 | Scheduler_OnOffUnit.Scheduler_1.CurrDateTime_Sched.WkDay |  | UInt |  | HoldingRegister | 2289
2647 | Scheduler_OnOffUnit.Scheduler_1.CopyTo_Day | SCH - Scheduller - Time Band - Copy to Day | DInt | ReadWrite | HoldingRegister | 2290 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN 7 - ALL
2648 | Scheduler_OnOffUnit.Scheduler_1.Day | SCH - Scheduller - Time Band - Day | DInt | ReadWrite | HoldingRegister | 2292 |  | 0 - MON 1 - TUE 2 - WED 3 - THU 4 - FRI 5 - SAT 6 - SUN
2649 | AlrmExhAirP_Msk | PAR - Fan - Return - Warning Threshold Air Pressure [Pa] | Real | ReadWrite | HoldingRegister | 2301 | Pa
2650 | AlrmSupplyAirP_Msk | PAR - Fan - Supply - Warning Threshold Air Pressure [Pa] | Real | ReadWrite | HoldingRegister | 2303 | Pa
2651 | AFreezeExtMaxTemp | PAR - Heating - Antifreeze - External Temperature - Maximum [°C] | Real | ReadWrite | HoldingRegister | 2305 | °C
2652 | AFreezeExtMinTemp | PAR - Heating - Antifreeze - External Temperature - Minimum [°C] | Real | ReadWrite | HoldingRegister | 2307 | °C
2653 | AfreezeHeatMax | PAR - Heating - Antifreeze - Valve Open - Maximum [%] | Real | ReadWrite | HoldingRegister | 2309 | % | 0 - 100 %
2654 | AFreezeHeatMaxT | PAR - Heating - Antifreeze - Time - Maximum [sec.] | UInt | ReadWrite | HoldingRegister | 2311 | sec.
2655 | AfreezeHeatMin | PAR - Heating - Antifreeze - Valve Open - Minimum [%] | Real | ReadWrite | HoldingRegister | 2312 | % | 0 - 100 %
2656 | AFreezeHeatMinT | PAR - Heating - Antifreeze - Time - Minimum [sec.] | UInt | ReadWrite | HoldingRegister | 2314 | sec.
2657 | AlrmExhAirP | PAR - Fan - Return - Warning Threshold Pressure [Pa] | Real | ReadWrite | HoldingRegister | 2315 | Pa
2658 | AlrmSupplyAirP | PAR - Fan - Supply - Warning Threshold Pressure [Pa] | Real | ReadWrite | HoldingRegister | 2317 | Pa
2659 | Cool_1.Man | PAR - Cooling - Main Cooler - Manual Digital | USInt | ReadWrite | HoldingRegister | 2319 |  | 0 - AUTO 1 - OFF 2 - ON
2660 | Cool_2.Man | PAR - Cooling - Main Cooler DX - Manual Digital | USInt | ReadWrite | HoldingRegister | 2320 |  | 0 - AUTO 1 - OFF 2 - ON
2661 | CoolDX_ResTyp | PAR - Cooling - Main Cooler DX - Operating Block | USInt | ReadWrite | HoldingRegister | 2321 |  | 0 - NONE 1 - ECO 2 - ECO + OPTIMAL
2662 | CoolExtTempThrsh | PAR - Regulation - ChangeOver - External Temperature - Cool Threshold [°C] | Real | ReadWrite | HoldingRegister | 2322 | °C
2663 | CoolMinOffT | PAR - Cooling - Main Cooler DX - Time - Minimum OFF [sec.] | UInt | ReadWrite | HoldingRegister | 2324 | sec.
2664 | CoolMinOnOnSameT | PAR - Cooling - Main Cooler DX - Time - Between starts [sec.] | UInt | ReadWrite | HoldingRegister | 2325 | sec.
2665 | CoolMinOnT | PAR - Cooling - Main Cooler DX - Time - Minimum ON [sec.] | UInt | ReadWrite | HoldingRegister | 2326 | sec.
2666 | CoolVlv.Man | PAR - Cooling - Main Cooler - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2327 | % | 0 - 100 %
2667 | DeltaDew_PID.Kp | PAR - Regulation PID - Humidity - Dewpoint - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2328 | Kp
2668 | DeltaDew_PID.Ti | PAR - Regulation PID - Humidity - Dewpoint - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2330 | Ti - sec.
2669 | DeltaDewTemp | PAR - Regulation PID - Humidity - Dewpoint - Delta [%] | Real | ReadWrite | HoldingRegister | 2331 | % | 0 - 100 %
2670 | DevCfg_PID_Seq_CO2[0].Kp | PAR - Regulation PID - CO2 Mixing - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2333 | Kp
2671 | DevCfg_PID_Seq_CO2[0].Ti | PAR - Regulation PID - CO2 Mixing - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2335 | Ti - sec.
2672 | DevCfg_PID_Seq_CO2[1].Kp | PAR - Regulation PID - CO2 Fan Compensation - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2336 | Kp
2673 | DevCfg_PID_Seq_CO2[1].Ti | PAR - Regulation PID - CO2 Fan Compensation - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2338 | Ti - sec.
2674 | DevCfg_PID_Seq_Cool[2].Kp | PAR - Regulation PID - Recovery - Cooling - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2339 | Kp
2675 | DevCfg_PID_Seq_Cool[2].Ti | PAR - Regulation PID - Recovery - Cooling - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2341 | Ti - sec.
2676 | DevCfg_PID_Seq_Cool[4].Kp | PAR - Regulation PID - Main Cooler - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2342 | Kp
2677 | DevCfg_PID_Seq_Cool[4].Ti | PAR - Regulation PID - Main Cooler - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2344 | Ti - sec.
2678 | DevCfg_PID_Seq_Cool[5].Kp | PAR - Regulation PID - Mixing - Cooling - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2345 | Kp
2679 | DevCfg_PID_Seq_Cool[5].Ti | PAR - Regulation PID - Mixing - Cooling - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2347 | Ti - sec.
2680 | DevCfg_PID_Seq_Heat[2].Kp | PAR - Regulation PID - Recovery - Heating - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2348 | Kp
2681 | DevCfg_PID_Seq_Heat[2].Ti | PAR - Regulation PID - Recovery - Heating - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2350 | Ti - sec.
2682 | DevCfg_PID_Seq_Heat[4].Kp | PAR - Regulation PID - Main Heater - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2351 | Kp
2683 | DevCfg_PID_Seq_Heat[4].Ti | PAR - Regulation PID - Main Heater - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2353 | Ti - sec.
2684 | DevCfg_PID_Seq_Heat[5].Kp | PAR - Regulation PID - Mixing - Heating - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2354 | Kp
2685 | DevCfg_PID_Seq_Heat[5].Ti | PAR - Regulation PID - Mixing - Heating - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2356 | Ti - sec.
2686 | DevCfg_PID_Seq_Heat[6].Kp | PAR - Regulation PID - ReHeating - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2357 | Kp
2687 | DevCfg_PID_Seq_Heat[6].Ti | PAR - Regulation PID - ReHeating - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2359 | Ti - sec.
2688 | DOff_ExhFan | PAR - Fan - Return - Time - OFF Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2360 | sec.
2689 | DOff_SupplyFan | PAR - Fan - Supply - Time - OFF Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2361 | sec.
2690 | DT_ChangeHum | PAR - Humidity - Time - Change Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2362 | sec.
2691 | DT_Dmp | PAR - Fan - Supply - Time - OFF Damper [sec.] | UInt | ReadWrite | HoldingRegister | 2363 | sec.
2692 | DT_ExhFan | PAR - Fan - Return - Time - ON Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2364 | sec.
2693 | DT_SupplyFan | PAR - Fan - Supply - Time - ON Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2365 | sec.
2694 | ExhAirFlowSet_Msk | PAR - Fan - Return - Flow - Maximum [m3/h] | Real | ReadWrite | HoldingRegister | 2366 | m3/h
2695 | ExhAirPSet_Msk | PAR - Fan - Return - Pressure - Maximum [Pa] | Real | ReadWrite | HoldingRegister | 2368 | Pa
2696 | FastCoolThrsh | PAR - Recovery - Cooling Limit [%] | Real | ReadWrite | HoldingRegister | 2370 | % | 0 - 100 %
2697 | FastHeatT | PAR - Recovery - Startup Time [sec.] | UInt | ReadWrite | HoldingRegister | 2372 | sec.
2698 | FastHeatThrsh | PAR - Recovery - Heating Limit [%] | Real | ReadWrite | HoldingRegister | 2373 | % | 0 - 100 %
2699 | FilterF7_Max | PAR - Filter - Maximum pressure F7 [Pa] | Real | ReadWrite | HoldingRegister | 2375 | Pa
2700 | FilterF9_Max | PAR - Filter - Maximum pressure F9 [Pa] | Real | ReadWrite | HoldingRegister | 2377 | Pa
2701 | FilterPG4_Max | PAR - Filter - Maximum pressure PG4 [Pa] | Real | ReadWrite | HoldingRegister | 2379 | Pa
2702 | FilterRet_Type | PAR - Filter - Return type | Int | ReadWrite | HoldingRegister | 2381 |  | 0 - None 1 - PG4/G4 2 - M5/F7 3 - F9
2703 | FilterSup_Type | PAR - Filter - Supply type | Int | ReadWrite | HoldingRegister | 2382 |  | 0 - None 1 - PG4/G4 2 - M5/F7 3 - F9
2704 | FireExhSpeed | PAR - Fan - Fire Setting - Return Speed [%] | Real | ReadWrite | HoldingRegister | 2383 | % | 0 - 100 %
2705 | FireSupplySpeed | PAR - Fan - Fire Setting - Supply Speed [%] | Real | ReadWrite | HoldingRegister | 2385 | % | 0 - 100 %
2706 | FireThrsh | PAR - Fan - Fire Setting - Threshold [°C] | Real | ReadWrite | HoldingRegister | 2387 | °C
2707 | HE_Pwr[0] | PAR - Heating - Main Heater - Maximum Power Modulating [%] | Real | ReadWrite | HoldingRegister | 2389 | % | 0 - 100 %
2708 | HE_Pwr[1] | PAR - Heating - Main Heater - Maximum Power 1 Stage [%] | Real | ReadWrite | HoldingRegister | 2391 | % | 0 - 100 %
2709 | HE_Pwr[2] | PAR - Heating - Main Heater - Maximum Power 2 Stage [%] | Real | ReadWrite | HoldingRegister | 2393 | % | 0 - 100 %
2710 | Heat_2.Man | PAR - Heating - Main Device 2 - Manual Digital | USInt | ReadWrite | HoldingRegister | 2395 |  | 0 - AUTO 1 - OFF 2 - ON
2711 | HeatExtTempThrsh | PAR - Regulation - ChangeOver - External Temperature - Heat Threshold [°C] | Real | ReadWrite | HoldingRegister | 2396 | °C
2712 | HeatMinOffT | PAR - Heating - Main Heater DX - Time - Minimum OFF [sec.] | UInt | ReadWrite | HoldingRegister | 2398 | sec.
2713 | HeatMinOnOnSameT | PAR - Heating - Main Heater DX - Time - Between starts [sec.] | UInt | ReadWrite | HoldingRegister | 2399 | sec.
2714 | HeatMinOnT | PAR - Heating - Main Heater DX - Time - Minimum ON [sec.] | UInt | ReadWrite | HoldingRegister | 2400 | sec.
2715 | HeatRecovery.Man | PAR - Recovery - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2401 | % | 0 - 100 %
2716 | HeatVlv.Man | PAR - Heating - Main Heater - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2402 | % | 0 - 100 %
2717 | Hum.Man | PAR - Humidity - Manual Digital | USInt | ReadWrite | HoldingRegister | 2403 |  | 0 - AUTO 1 - OFF 2 - ON
2718 | Hum_PID.DeadBand | PAR - Regulation PID - Humidity - DeadBand [g/m3] | Real | ReadWrite | HoldingRegister | 2404 | g/m3
2719 | Hum_PID.Kp | PAR - Regulation PID - Humidity - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2406 | Kp
2720 | Hum_PID.Ti | PAR - Regulation PID - Humidity - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2408 | Ti - sec.
2721 | HW_Set | PAR - Heating - Main Water - SetPoint [°C] | Real | ReadWrite | HoldingRegister | 2409 | °C
2722 | IdleT_ExhFan | PAR - Fan - Return - Idle Time [sec.] | UInt | ReadWrite | HoldingRegister | 2411 | sec.
2723 | IdleT_SupplyFan | PAR - Fan - Supply - Idle Time [sec.] | UInt | ReadWrite | HoldingRegister | 2412 | sec.
2724 | K_FactorExh | PAR - Fan - Return - K-Factor | Real | ReadWrite | HoldingRegister | 2413
2725 | K_FactorExhCode | PAR - Fan - Return - Fan Code | USInt | ReadWrite | HoldingRegister | 2415 |  | 0 - CUSTOM 1 - VS-225 2 - VS-250 3 - VS-315 4 - VS-355 5 - VS-400 6 - VS-450 7 - VS-500 8 - VS-560 9 - VS-630
2726 | K_FactorSupply | PAR - Fan - Supply - K-Factor | Real | ReadWrite | HoldingRegister | 2416
2727 | K_FactorSupplyCode | PAR - Fan - Supply - Fan Code | USInt | ReadWrite | HoldingRegister | 2418 |  | 0 - CUSTOM 1 - VS-225 2 - VS-250 3 - VS-315 4 - VS-355 5 - VS-400 6 - VS-450 7 - VS-500 8 - VS-560 9 - VS-630
2728 | LowSupplyTempThrsh | PAR - Heating - Supply Limit - Threshold [°C] | Real | ReadWrite | HoldingRegister | 2419 | °C
2729 | MainCoolMin | PAR - Cooling - Main Cooler - Minimum Power [%] | Real | ReadWrite | HoldingRegister | 2421 | % | 0 - 100 %
2730 | MainCW_MinPID | PAR - Cooling - Main Cooler Water - Minimum Valve Signal [%] | Real | ReadWrite | HoldingRegister | 2423 | % | 0 - 100 %
2731 | MainHeatMin | PAR - Heating - Main Heater - Minimum Power [%] | Real | ReadWrite | HoldingRegister | 2425 | % | 0 - 100 %
2732 | MainHW_MinPID | PAR - Heating - Main Water - Minimum Valve Singal [%] | Real | ReadWrite | HoldingRegister | 2427 | % | 0 - 100 %
2733 | ManExhFanIdle | PAR - Fan - Return - Idle Power [%] | Real | ReadWrite | HoldingRegister | 2429 | % | 0 - 100 %
2734 | ManSupplyFanIdle | PAR - Fan - Supply - Idle Power [%] | Real | ReadWrite | HoldingRegister | 2431 | % | 0 - 100 %
2735 | MinHeatRec | PAR - Recovery - Heating - Minimum Power [%] | Real | ReadWrite | HoldingRegister | 2433 | % | 0 - 100 %
2736 | ModulHum.Man | PAR - Humidity - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2435 | % | 0 - 100 %
2737 | ModulMixDamp.Man | PAR - Mix Damper - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2436 | % | 0 - 100 %
2738 | ModulMixDampMaxVal | PAR - Mix Damper - Limits - Maximum Openning [%] | Real | ReadWrite | HoldingRegister | 2437 | % | 0 - 100 %
2739 | ModulMixDampMinVal | PAR - Mix Damper - Limits - Minimum Openning [%] | Real | ReadWrite | HoldingRegister | 2439 | % | 0 - 100 %
2740 | ModulPreHeat.Man | PAR - Heating - PreHeating - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2441 | % | 0 - 100 %
2741 | NightKickHour | PAR - System - Night Kick Time - Hour [h] | UInt | ReadWrite | HoldingRegister | 2442 | h
2742 | NightKickMinute | PAR - System - Night Kick Time - Minute [min.] | UInt | ReadWrite | HoldingRegister | 2443 | min.
2743 | PID_Exh.Kp | PAR - Regulation PID - Fan Return - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2444 | Kp
2744 | PID_Exh.Td | PAR - Regulation PID - Fan Return - Derivative time [Td - sec.] | UInt | ReadWrite | HoldingRegister | 2446 | Td - sec.
2745 | PID_Exh.Ti | PAR - Regulation PID - Fan Return - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2447 | Ti - sec.
2746 | PID_FrostProt.Kp | PAR - Regulation PID - Recovery - Frost - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2448 | Kp
2747 | PID_FrostProt.SetP | PAR - Recovery - Frost Protection - SetPoint [°C] | Real | ReadWrite | HoldingRegister | 2450 | °C
2748 | PID_FrostProt.Ti | PAR - Regulation PID - Recovery - Frost - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2452 | Ti - sec.
2749 | PID_HeatHW.Kp | PAR - Regulation PID - Main Water - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2453 | Kp
2750 | PID_HeatHW.Ti | PAR - Regulation PID - Main Water - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2455 | Ti - sec.
2751 | PID_PreHeatCoil.Kp | PAR - Regulation PID - PreHeating - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2456 | Kp
2752 | PID_PreHeatCoil.Ti | PAR - Regulation PID - PreHeating - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2458 | Ti - sec.
2753 | PID_PreHeatHW.Kp | PAR - Regulation PID - PreHeater Water - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2459 | Kp
2754 | PID_PreHeatHW.Ti | PAR - Regulation PID - PreHeater Water - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2461 | Ti - sec.
2755 | PID_Supply.Kp | PAR - Regulation PID - Fan Supply - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2462 | Kp
2756 | PID_Supply.Td | PAR - Regulation PID - Fan Supply - Derivative time [Td - sec.] | UInt | ReadWrite | HoldingRegister | 2464 | Td - sec.
2757 | PID_Supply.Ti | PAR - Regulation PID - Fan Supply - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2465 | Ti - sec.
2758 | PreHeaterPump.Man | PAR - Heating - PreHeating - Manual Digital | USInt | ReadWrite | HoldingRegister | 2466 |  | 0 - AUTO 1 - OFF 2 - ON
2759 | PreHeatHE_Pwr[0] | PAR - Heating - PreHeating - Maximum Power Modulating [%] | Real | ReadWrite | HoldingRegister | 2467 | % | 0 - 100 %
2760 | PreHeatHE_Pwr[1] | PAR - Heating - PreHeating - Maximum Power 1 Stage [%] | Real | ReadWrite | HoldingRegister | 2469 | % | 0 - 100 %
2761 | PreHeatMin | PAR - Heating - PreHeating - Minimum Power [%] | Real | ReadWrite | HoldingRegister | 2471 | % | 0 - 100 %
2762 | PreHeatMinOffT | PAR - Heating - PreHeating DX - Time - Minimum OFF [sec.] | UInt | ReadWrite | HoldingRegister | 2473 | sec.
2763 | PreheatMinOnOnSameT | PAR - Heating - PreHeating DX - Time - Between starts [sec.] | UInt | ReadWrite | HoldingRegister | 2474 | sec.
2764 | PreHeatMinOnT | PAR - Heating - PreHeating DX - Time - Minimum ON [sec.] | UInt | ReadWrite | HoldingRegister | 2475 | sec.
2765 | PreHeatRotConf.DevNoPerCirc | PAR - Heating - PreHeating - Type | Int | ReadWrite | HoldingRegister | 2476 |  | 1 - MODULATING 2 - MOD. + 1 STAGE
2766 | PreHeatSet | PAR - Heating - PreHeater Water - SetPoint [°C] | Real | ReadWrite | HoldingRegister | 2477 | °C
2767 | PreHW_MinPID | PAR - Heating - PreHeater Water - Minimum Valve Signal [%] | Real | ReadWrite | HoldingRegister | 2479 | % | 0 - 100 %
2768 | Rec_MinPID | PAR - Recovery - Heating - Minimum Recovery [%] | Real | ReadWrite | HoldingRegister | 2481 | % | 0 - 100 %
2769 | RecoveryPump.Man | PAR - Recovery - Manual Digital | USInt | ReadWrite | HoldingRegister | 2483 |  | 0 - AUTO 1 - OFF 2 - ON
2770 | ReHeat.Man | PAR - Heating - ReHeating - Manual Digital | USInt | ReadWrite | HoldingRegister | 2484 |  | 0 - AUTO 1 - OFF 2 - ON
2771 | ReHeatHE_Pwr[0] | PAR - Heating - ReHeating - Maximum Power Modulating [%] | Real | ReadWrite | HoldingRegister | 2485 | % | 0 - 100 %
2772 | ReHeatHE_Pwr[1] | PAR - Heating - ReHeating - Maximum Power 1 Stage [%] | Real | ReadWrite | HoldingRegister | 2487 | % | 0 - 100 %
2773 | ReHeatMin | PAR - Heating - ReHeating - Minimum Power [%] | Real | ReadWrite | HoldingRegister | 2489 | % | 0 - 100 %
2774 | ReHeatMinOffT | PAR - Heating - ReHeater DX - Time - Minimum OFF [sec.] | UInt | ReadWrite | HoldingRegister | 2491 | sec.
2775 | ReHeatMinOnOnSameT | PAR - Heating - ReHeater DX - Time - Between starts [sec.] | UInt | ReadWrite | HoldingRegister | 2492 | sec.
2776 | ReHeatMinOnT | PAR - Heating - ReHeater DX - Time - Minimum ON [sec.] | UInt | ReadWrite | HoldingRegister | 2493 | sec.
2777 | ReHeatRotConf.CompMinPwr | PAR - Heating - ReHeating - Minimum Power [%] | Int | ReadWrite | HoldingRegister | 2494 | % | 0 - 100 %
2778 | ReHeatRotConf.DevNoPerCirc | PAR - Heating - ReHeating - Type | Int | ReadWrite | HoldingRegister | 2495 |  | 1 - MODULATING 2 - MOD. + 1 STAGE
2779 | ReHeatVlv.Man | PAR - Heating - ReHeating - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2496 | % | 0 - 100 %
2780 | ReHW_MinPID | PAR - Heating - ReHeating - Minimum Valve Signal [%] | Real | ReadWrite | HoldingRegister | 2497 | % | 0 - 100 %
2781 | Ret_NrPole | PAR - Fan - Return - Number of pole | Real | ReadWrite | HoldingRegister | 2499
2782 | RevOut_1.Man | PAR - Heating - Reverse Device 1 - Manual Digital | USInt | ReadWrite | HoldingRegister | 2501 |  | 0 - AUTO 1 - OFF 2 - ON
2783 | RevOut_2.Man | PAR - Heating - Reverse Device 2 - Manual Digital | USInt | ReadWrite | HoldingRegister | 2502 |  | 0 - AUTO 1 - OFF 2 - ON
2784 | RevOutVlv.Man | PAR - Heating - Reverse Device 1 - Manual Analog [%] | USInt | ReadWrite | HoldingRegister | 2503 | % | 0 - 100 %
2785 | RoomReg_SetP_Offs_Kp | PAR - Regulation PID - Room Compnsation - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2504 | Kp
2786 | RoomReg_SetP_Offs_Ti | PAR - Regulation PID - Room Compnsation - Integral time [sec.] | UInt | ReadWrite | HoldingRegister | 2506 | sec.
2787 | RotConf.CompMinPwr | PAR - Heating - Main Heater - Minimum Power [%] | Int | ReadWrite | HoldingRegister | 2507 | % | 0 - 100 %
2788 | RotConf.DevNoPerCirc | PAR - Heating - Main Heater - Type | Int | ReadWrite | HoldingRegister | 2508 |  | 1 - MODULATING 2 - MOD. + 1 STAGE 3 - MOD. + 2 STAGES
2789 | RRG_NrPole | PAR - Recovery - Rotary - Numver of pole | Real | ReadWrite | HoldingRegister | 2509
2790 | SetMaxLimit | PAR - Regulation - Limits - Return / Room - Maximum [°C] | Real | ReadWrite | HoldingRegister | 2511 | °C
2791 | SetMinLimit | PAR - Regulation - Limits - Return / Room - Minimum [°C] | Real | ReadWrite | HoldingRegister | 2513 | °C
2792 | StandbyT | PAR - System - StandBy - Time [sec.] | UInt | ReadWrite | HoldingRegister | 2515 | sec.
2793 | StartHumPerc | PAR - Humidity - Digital - Start [%] | Real | ReadWrite | HoldingRegister | 2516 | % | 0 - 100 %
2794 | StopHumPerc | PAR - Humidity - Digital - Stop [%] | Real | ReadWrite | HoldingRegister | 2518 | % | 0 - 100 %
2795 | Sup_NrPole | PAR - Fan - Supply - Number of pole | Real | ReadWrite | HoldingRegister | 2520
2796 | SupplyAirFlowSet_Msk | PAR - Fan - Return - Flow - Maximum [m3/h] | Real | ReadWrite | HoldingRegister | 2522 | m3/h
2797 | SupplyAirPSet_Msk | PAR - Fan - Supply - Pressure - Maximum [Pa] | Real | ReadWrite | HoldingRegister | 2524 | Pa
2798 | SupplyDewPoint | PAR - Humidity - Supply Dewpoint [°C] | Real | ReadWrite | HoldingRegister | 2526 | °C
2799 | SupplyFanMax | PAR - CO2 - Fan Compensation - Max Air-Flow Quality [%] | Real | ReadWrite | HoldingRegister | 2528 | % | 0 - 100 %
2800 | SupplyMaxSet | PAR - Regulation - Limits - Temperature Supply - Maximum [°C] | Real | ReadWrite | HoldingRegister | 2530 | °C
2801 | SupplyMinSet | PAR - Regulation - Limits - Temperature Supply - Minimum [°C] | Real | ReadWrite | HoldingRegister | 2532 | °C
2802 | SupplyTemp_CoolHeatDT | PAR - Regulation - ChangeOver - External Temperature - Time Delay [sec.] | UInt | ReadWrite | HoldingRegister | 2534 | sec.
2803 | ThrshOffCool_1 | PAR - Cooling - Main Cooler DX - Stop Step 1 [%] | Real | ReadWrite | HoldingRegister | 2535 | % | 0 - 100 %
2804 | ThrshOffCool_2 | PAR - Cooling - Main Cooler DX - Stop Step 2 [%] | Real | ReadWrite | HoldingRegister | 2537 | % | 0 - 100 %
2805 | ThrshOffHeat_1 | PAR - Heating - Main Heater DX - Stop Step 1 [%] | Real | ReadWrite | HoldingRegister | 2539 | % | 0 - 100 %
2806 | ThrshOffHeat_2 | PAR - Heating - Main Heater DX - Stop Step 2 [%] | Real | ReadWrite | HoldingRegister | 2541 | % | 0 - 100 %
2807 | ThrshOnCool_1 | PAR - Cooling - Main Cooler DX - Start Step 1 [%] | Real | ReadWrite | HoldingRegister | 2543 | % | 0 - 100 %
2808 | ThrshOnCool_2 | PAR - Cooling - Main Cooler DX - Start Step 2 [%] | Real | ReadWrite | HoldingRegister | 2545 | % | 0 - 100 %
2809 | ThrshOnHeat_1 | PAR - Heating - Main Heater DX - Start Step 1 [%] | Real | ReadWrite | HoldingRegister | 2547 | % | 0 - 100 %
2810 | ThrshOnHeat_2 | PAR - Heating - Main Heater DX - Start Step 2 [%] | Real | ReadWrite | HoldingRegister | 2549 | % | 0 - 100 %
2811 | W_HeatFreezeSet | PAR - Heating - Main Water - Frreeze SetPoint [°C] | Real | ReadWrite | HoldingRegister | 2551 | °C
2812 | W_PreHeatFreezeSet | PAR - Heating - PreHeater Water - Freeze SetPoint [°C] | Real | ReadWrite | HoldingRegister | 2553 | °C
2813 | WakeUpT | PAR - System - Wake Up - Time [sec.] | UInt | ReadWrite | HoldingRegister | 2555 | sec.
2814 | WarnThrshExhFlw_Msk | PAR - Fan - Return - Warning Threshold Air Flow [m3/h] | Real | ReadWrite | HoldingRegister | 2556 | m3/h
2815 | WarnThrshSupplyFlw_Msk | PAR - Fan - Supply - Warning Threshold Air Flow [m3/h] | Real | ReadWrite | HoldingRegister | 2558 | m3/h
2816 | AbsHum | PAR - Humidity - ABS Humidity [g/m3] | Real | Read | HoldingRegister | 2560 | g/m3
2817 | AbsHumSet | PAR - Humidity - ABS SetPoint [g/m3] | Real | Read | HoldingRegister | 2562 | g/m3
2818 | AfterPreHeatReq | PAR - Regulation PID - PreHeating - Output [%] | Real | Read | HoldingRegister | 2564 | % | 0 - 100 %
2819 | AirQualFan | PAR - Regulation PID - CO2 Fan Compensation - Output [%] | Real | Read | HoldingRegister | 2566 | % | 0 - 100 %
2820 | AirQualReq_1 | PAR - Regulation PID - CO2 Mixing - Output [%] | Real | Read | HoldingRegister | 2568 | % | 0 - 100 %
2821 | Cooling_PID_Seq[2] | PAR - Regulation PID - Recovery - Cooling - Output [%] | Real | Read | HoldingRegister | 2570 | % | 0 - 100 %
2822 | Cooling_PID_Seq[3] | PAR - Regulation PID - Reverse - Cooling - Output [%] | Real | Read | HoldingRegister | 2572 | % | 0 - 100 %
2823 | Cooling_PID_Seq[4] | PAR - Regulation PID - Main Cooler - Output [%] | Real | Read | HoldingRegister | 2574 | % | 0 - 100 %
2824 | Cooling_PID_Seq[5] | PAR - Regulation PID - Mixing - Cooling - Output [%] | Real | Read | HoldingRegister | 2576 | % | 0 - 100 %
2825 | FrostProtReq | PAR - Regulation PID - Recovery - Frost - Output [%] | Real | Read | HoldingRegister | 2578 | % | 0 - 100 %
2826 | Heating_PID_Seq[2] | PAR - Regulation PID - Recovery - Heating - Output [%] | Real | Read | HoldingRegister | 2580 | % | 0 - 100 %
2827 | Heating_PID_Seq[3] | PAR - Regulation PID - Reverse - Heating - Output [%] | Real | Read | HoldingRegister | 2582 | % | 0 - 100 %
2828 | Heating_PID_Seq[4] | PAR - Regulation PID - Main Heater - Output [%] | Real | Read | HoldingRegister | 2584 | % | 0 - 100 %
2829 | Heating_PID_Seq[5] | PAR - Regulation PID - Mixing - Heating - Output [%] | Real | Read | HoldingRegister | 2586 | % | 0 - 100 %
2830 | Heating_PID_Seq[6] | PAR - Regulation PID - ReHeating - Output [%] | Real | Read | HoldingRegister | 2588 | % | 0 - 100 %
2831 | Heating_PID_Seq[7] | PAR - Regulation PID - Fan Heating - Output [%] | Real | Read | HoldingRegister | 2590 | % | 0 - 100 %
2832 | HumDehumReq | PAR - Regulation PID - Humidity - Output [%] | Real | Read | HoldingRegister | 2592 | % | 0 - 100 %
2833 | HW_AfreezeReq | PAR - Regulation PID - Main Water - Output [%] | Real | Read | HoldingRegister | 2594 | % | 0 - 100 %
2834 | PID_DewCompens | PAR - Regulation PID - Humidity - Dewpoint - Output [%] | Real | Read | HoldingRegister | 2596 | % | 0 - 100 %
2835 | PID_RegCompens | PAR - Regulation PID - Room Compnsation - Output [%] | Real | Read | HoldingRegister | 2598 | % | 0 - 100 %
2836 | PreW_AfreezeReq | PAR - Regulation PID - PreHeater Water - Output [%] | Real | Read | HoldingRegister | 2600 | % | 0 - 100 %
2837 | MainHeatMax | PAR - Heating - Main Heater - Maximum Power [%] | Real | ReadWrite | HoldingRegister | 2602 | % | 0 - 100 %
2838 | RevHeat_Sig_Min | PAR - Heating - Reverse Device 1 - Heating - Minimum signal [%] | Real | ReadWrite | HoldingRegister | 2604 | % | 0 - 100 %
2839 | RevHeat_Sig_Max | PAR - Heating - Reverse Device 1 - Heating - Maximum signal [%] | Real | ReadWrite | HoldingRegister | 2606 | % | 0 - 100 %
2840 | RevCool_Sig_Min | PAR - Heating - Reverse Device 1 - Cooling - Minimum signal [%] | Real | ReadWrite | HoldingRegister | 2608 | % | 0 - 100 %
2841 | RevCool_Sig_Max | PAR - Heating - Reverse Device 1 - Cooling - Maximum signal [%] | Real | ReadWrite | HoldingRegister | 2610 | % | 0 - 100 %
2842 | RevTemp_En | PAR - Heating - Reverse Device 1 - Permistion from external temperature [°C] | Real | ReadWrite | HoldingRegister | 2612 | °C
2843 | ReHeatMax | PAR - Heating - ReHeating - Maximum Power [%] | Real | ReadWrite | HoldingRegister | 2614 | % | 0 - 100 %
2844 | PreHeatMax | PAR - Heating - PreHeating - Maximum Power [%] | Real | ReadWrite | HoldingRegister | 2616 | % | 0 - 100 %
2845 | LowTempAlrmDT_Run | PAR - Heating - Supply Limit - Threshold delay [sec.] | UInt | ReadWrite | HoldingRegister | 2618 | sec.
2846 | MainStartupValue | PAR - Heating - Main Heater HW - Pre-Heat always start - Minimum signal [%] | Real | ReadWrite | HoldingRegister | 2619 | % | 0 - 100 %
2847 | HE_Alarm_Delay | PAR - Heating - Main Heater HE - Alarm delay [sec.] | UInt | ReadWrite | HoldingRegister | 2621 | sec.
2848 | Pump_ExtTemp | PAR - Heating - Main Heater HW - Active pump when external temp lower [°C] | Real | ReadWrite | HoldingRegister | 2622 | °C
2849 | Valve_ExtTemp | PAR - Heating - Main Heater HW - Active vavlve when external temp lower [°C] | Real | ReadWrite | HoldingRegister | 2624 | °C
2850 | MainHW_MinPID_Text | PAR - Heating - Main Heater HW - Minimum signal for winter valve [%] | Real | ReadWrite | HoldingRegister | 2626 | % | 0 - 100 %
2851 | DoubleFanRotT | PAR - Fan - Redundant - Time rotation [h] | USInt | ReadWrite | HoldingRegister | 2628 | h
2852 | DoubleDamp.Man | PAR - Fan - Redundant - Manual Digital | USInt | ReadWrite | HoldingRegister | 2629 |  | 0 - AUTO 1 - OFF 2 - ON
2853 | FanTempReg_Sig | PAR - Fan - Temperature regulation - Output [%] | Real | ReadWrite | HoldingRegister | 2630 | % | 0 - 100 %
2854 | DevCfg_PID_Seq_Heat[7].Kp | PAR - Fan - Temperature regulation - Proportional gain [Kp] | Real | ReadWrite | HoldingRegister | 2632 | Kp
2855 | DevCfg_PID_Seq_Heat[7].Ti | PAR - Fan - Temperature regulation - Integral time [Ti - sec.] | UInt | ReadWrite | HoldingRegister | 2634 | Ti - sec.
2856 | FanTempReg_Max | PAR - Fan - Temperature regulation - Maximum fan signal correction [%] | Real | ReadWrite | HoldingRegister | 2635 | % | 0 - 100 %
2857 | RRG_MinValueFor_Al | PAR - Recovery - Rotery - Minium signal for active power [%] | Real | ReadWrite | HoldingRegister | 2637 | % | 0 - 100 %
2858 | RRG_MinPower_Al | PAR - Recovery - Rotery - Minimum power for alarm [W] | Real | ReadWrite | HoldingRegister | 2639 | W
2859 | Mix_Val_ECO | PAR - Mixing - Manual mode ECO - Signal [%] | Real | ReadWrite | HoldingRegister | 2641 | % | 0 - 100 %
2860 | Mix_Val_OPTIMAL | PAR - Mixing - Manual mode Optimal - Signal [%] | Real | ReadWrite | HoldingRegister | 2643 | % | 0 - 100 %
2861 | Mix_Val_COMFORT | PAR - Mixing - Manual mode Comfort - Signal [%] | Real | ReadWrite | HoldingRegister | 2645 | % | 0 - 100 %
2862 | AFreezeHeatOut | PAR - Heater - Antifreeze - Output [%] | Real | ReadWrite | HoldingRegister | 2647 | % | 0 - 100 %
2863 | AFreezeHeatOutT | PAR - Heater - Antifreeze - Output T [%] | UInt | ReadWrite | HoldingRegister | 2649 | % | 0 - 100 %
2864 | HW_Set_Read |  | Real |  | HoldingRegister | 2650
2865 | HW_Set_X1 |  | Real |  | HoldingRegister | 2652
2866 | HW_Set_X2 |  | Real |  | HoldingRegister | 2654
2867 | SupFilter_Warning |  | Real |  | HoldingRegister | 2656
2868 | RetFilter_Warning |  | Real |  | HoldingRegister | 2658
2869 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Fan_Supply |  | Real |  | HoldingRegister | 2660
2870 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Fan_Return |  | Real |  | HoldingRegister | 2662
2871 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Filter_Supply |  | Real |  | HoldingRegister | 2664
2872 | MB_Devices.MB_MainBoard_1.Offset_Pressure_Filter_Return |  | Real |  | HoldingRegister | 2666
2873 | FanSup_AI_X1 |  | Real |  | HoldingRegister | 2668
2874 | FanSup_AI_X2 |  | Real |  | HoldingRegister | 2670
2875 | FanSup_AI_Y1 |  | Real |  | HoldingRegister | 2672
2876 | FanSup_AI_Y2 |  | Real |  | HoldingRegister | 2674
2877 | FanRet_AI_X1 |  | Real |  | HoldingRegister | 2676
2878 | FanRet_AI_X2 |  | Real |  | HoldingRegister | 2678
2879 | FanRet_AI_Y1 |  | Real |  | HoldingRegister | 2680
2880 | FanRet_AI_Y2 |  | Real |  | HoldingRegister | 2682
2881 | FreezeAl_Text |  | Real |  | HoldingRegister | 2684
2882 | FreezeAl_Set |  | Real |  | HoldingRegister | 2686
2883 | HW_Set_Y2 |  | Real |  | HoldingRegister | 2688
2884 | HE_Fan_Delay |  | UDInt |  | HoldingRegister | 2690
2885 | H_Time_On_Delay |  | UDInt |  | HoldingRegister | 2692
2886 | FilterSup_Type_2 |  | Int |  | HoldingRegister | 2694
2887 | FilterSup_Type_3 |  | Int |  | HoldingRegister | 2695
2888 | FilterRet_Type_2 |  | Int |  | HoldingRegister | 2696
2889 | VFD_SupMax_RPM |  | Real |  | HoldingRegister | 2697
2890 | VFD_RetMax_RPM |  | Real |  | HoldingRegister | 2699
2891 | VFD_SupMax_Hz |  | Real |  | HoldingRegister | 2701
2892 | VFD_RetMax_Hz |  | Real |  | HoldingRegister | 2703
2893 | VFD_SupMax_RPM_2 |  | Int |  | HoldingRegister | 2705
2894 | VFD_RetMax_RPM_2 |  | Int |  | HoldingRegister | 2706
2895 | Add_Temp_1 |  | Real |  | HoldingRegister | 2707
2896 | Add_Temp_2 |  | Real |  | HoldingRegister | 2709
2897 | Add_Temp_3 |  | Real |  | HoldingRegister | 2711
2898 | Add_Humid_1 |  | Real |  | HoldingRegister | 2713
2899 | Add_Humid_2 |  | Real |  | HoldingRegister | 2715
2900 | Add_Humid_3 |  | Real |  | HoldingRegister | 2717
2901 | Add_Adr_1 |  | UDInt |  | HoldingRegister | 2719
2902 | Add_Adr_2 |  | UDInt |  | HoldingRegister | 2721
2903 | Add_Adr_3 |  | UDInt |  | HoldingRegister | 2723
2904 | Rec_ExtTemp |  | Real |  | HoldingRegister | 2725
2905 | Rec_MinExt |  | Real |  | HoldingRegister | 2727
2906 | Rec_MaxFrost |  | Real |  | HoldingRegister | 2729
2907 | FanTempReg_Sig_2 |  | Real |  | HoldingRegister | 2731
2908 | FanTempReg_Max_2 |  | Real |  | HoldingRegister | 2733
2909 | RegTemp | SP - Setpoint - Temperature - Current - Value [°C] | Real | ReadWrite | HoldingRegister | 2735 | °C
2910 | SetTyp | SP - Work Mode | USInt | ReadWrite | HoldingRegister | 2737 |  | 0 - OFF 1 - ECONOMY 3 - COMFORT 4 - STANDBY 5 - AUTO
2911 | UnitSetP.AirFlwSetP.Comfort | SP - Setpoint - Air Flow - Supply - 3 - Comfort [%] | Real | ReadWrite | HoldingRegister | 2738 | % | 0 - 100 %
2912 | UnitSetP.AirFlwSetP.Economy | SP - Setpoint - Air Flow - Supply - 1 - Economy [%] | Real | ReadWrite | HoldingRegister | 2740 | % | 0 - 100 %
2913 | UnitSetP.AirFlwSetP.PreComfort | SP - Setpoint - Air Flow - Supply - 2 - Optimal [%] | Real | ReadWrite | HoldingRegister | 2742 | % | 0 - 100 %
2914 | UnitSetP.AirQualitySetP.Comfort | SP - Setpoint - Air Quality - 3 - Comfort [ppm] | Real | ReadWrite | HoldingRegister | 2744 | ppm
2915 | UnitSetP.AirQualitySetP.Economy | SP - Setpoint - Air Quality - 1 - Economy [ppm] | Real | ReadWrite | HoldingRegister | 2746 | ppm
2916 | UnitSetP.AirQualitySetP.PreComfort | SP - Setpoint - Air Quality - 2 - Optimal [ppm] | Real | ReadWrite | HoldingRegister | 2748 | ppm
2917 | UnitSetP.HumSetP.Comfort | SP - Setpoint - Humidity - 3 - Comfort [%] | Real | ReadWrite | HoldingRegister | 2750 | % | 0 - 100 %
2918 | UnitSetP.HumSetP.Economy | SP - Setpoint - Humidity - 1 - Economy [%] | Real | ReadWrite | HoldingRegister | 2752 | % | 0 - 100 %
2919 | UnitSetP.HumSetP.PreComfort | SP - Setpoint - Humidity - 2 - Optimal [%] | Real | ReadWrite | HoldingRegister | 2754 | % | 0 - 100 %
2920 | UnitSetP.RetAirFlwSetP.Comfort | SP - Setpoint - Air Flow - Return - 3 - Comfort [%] | Real | ReadWrite | HoldingRegister | 2756 | % | 0 - 100 %
2921 | UnitSetP.RetAirFlwSetP.Economy | SP - Setpoint - Air Flow - Return - 1 - Economy [%] | Real | ReadWrite | HoldingRegister | 2758 | % | 0 - 100 %
2922 | UnitSetP.RetAirFlwSetP.PreComfort | SP - Setpoint - Air Flow - Return - 2 - Optimal [%] | Real | ReadWrite | HoldingRegister | 2760 | % | 0 - 100 %
2923 | UnitSetP.RoomTempSetP.Comfort | SP - Setpoint - Temperature - Room - 3 - Comfort [°C] | Real | ReadWrite | HoldingRegister | 2762 | °C
2924 | UnitSetP.RoomTempSetP.Economy | SP - Setpoint - Temperature - Room - 1 - Economy [°C] | Real | ReadWrite | HoldingRegister | 2764 | °C
2925 | UnitSetP.RoomTempSetP.PreComfort | SP - Setpoint - Temperature - Room - 2 - Optimal [°C] | Real | ReadWrite | HoldingRegister | 2766 | °C
2926 | ActualSet | SP - Setpoint - Temperature - Actual [°C] | Real | Read | HoldingRegister | 2768 | °C
2927 | CurrAirFlwSetP_Val | SP - Setpoint - Air Flow - Supply - Current - Value [%] | Real | Read | HoldingRegister | 2770 | % | 0 - 100 %
2928 | CurrAirQualitySetP_Val | SP - Setpoint - Air Quality - Current - Value [ppm] | Real | Read | HoldingRegister | 2772 | ppm
2929 | CurrHumSetP_Val | SP - Setpoint - Humidity - Current - Value [%] | Real | Read | HoldingRegister | 2774 | % | 0 - 100 %
2930 | CurrRetAirFlwSetP_Val | SP - Setpoint - Air Flow - Return - Current - Value [%] | Real | Read | HoldingRegister | 2776 | % | 0 - 100 %
2931 | CurrRoomTempSetP_Val | SP - Setpoint - Temperature - Room - Current - Value [°C] | Real | Read | HoldingRegister | 2778 | °C
2932 | UnitSetP_AirFlwSetP_Comfort | SP - Setpoint - Air Flow - Supply - 3 - Comfort (Actual) [%] | Real | Read | HoldingRegister | 2780 | % | 0 - 100 %
2933 | UnitSetP_AirFlwSetP_Comfort_2 | SP - Setpoint - Air Flow - Return - 3 - Comfort (Actual) [%] | Real | Read | HoldingRegister | 2782 | % | 0 - 100 %
2934 | UnitSetP_AirFlwSetP_Economy | SP - Setpoint - Air Flow - Supply - 1 - Economy (Actual [%] | Real | Read | HoldingRegister | 2784 | % | 0 - 100 %
2935 | UnitSetP_AirFlwSetP_Economy_2 | SP - Setpoint - Air Flow - Return - 1 - Economy (Actual [%] | Real | Read | HoldingRegister | 2786 | % | 0 - 100 %
2936 | UnitSetP_AirFlwSetP_PreComfort | SP - Setpoint - Air Flow - Supply - 2 - Optimal (Actual [%] | Real | Read | HoldingRegister | 2788 | % | 0 - 100 %
2937 | UnitSetP_AirFlwSetP_PreComfort_2 | SP - Setpoint - Air Flow - Return - 2 - Optimal (Actual [%] | Real | Read | HoldingRegister | 2790 | % | 0 - 100 %
2938 | RecHeat_PowerTemp_T_kWh | ECO - Power Cool [kW] | Real | Read | HoldingRegister | 2792 | kW
2939 | RecCool_PowerTemp_T_kWh | ECO - Power Cool [kWh] | Real | Read | HoldingRegister | 2794 | kWh
2940 | Heat_PowerTemp_T_kWh | ECO - Power Cost - Constant [kWh] | Real | Read | HoldingRegister | 2796 | kWh
2941 | Cool_PowerTemp_T_kWh | ECO - Power Cost - Constant - Mode ECO [kWh] | Real | Read | HoldingRegister | 2798 | kWh
2942 | PowerElect_T_kWh_ECO | ECO - Power Cost - Constant - Mode Optimal [kWh] | Real | Read | HoldingRegister | 2800 | kWh
2943 | PowerElect_T_kWh_Optimal | ECO - Power Cost - Constant - Mode Comfort [kWh] | Real | Read | HoldingRegister | 2802 | kWh
2944 | PowerElect_T_kWh_Comfort | ECO - Power Cost [kWh] | Real | Read | HoldingRegister | 2804 | kWh
2945 | SupplyFan_Power_E1 | ECO - Power Cost - Mode ECO [kWh] | Real | Read | HoldingRegister | 2806 | kWh
2946 | ReturnFan_Power_E1 | ECO - Power Cost - Mode Optimal [kWh] | Real | Read | HoldingRegister | 2808 | kWh
2947 | HC_Mode_ECO | ECO - Power Cost - Mode Comfort [kWh] | UDInt | Read | HoldingRegister | 2810 | kWh
2948 | HC_Mode_Comfort | ECO - Power Heat [kW] | UDInt | Read | HoldingRegister | 2812 | kW
2949 | HC_Mode_Optimal | ECO - Power Heat kWh [kWh] | UDInt | Read | HoldingRegister | 2814 | kWh
2950 | RecHeat_PowerTemp | ECO [kWh] | Real | Read | HoldingRegister | 2816 | kWh
2951 | RecCool_PowerTemp | ECO [kWh] | Real | Read | HoldingRegister | 2818 | kWh
2952 | Heat_PowerTemp | ECO [kWh] | Real | Read | HoldingRegister | 2820 | kWh
2953 | Cool_PowerTemp | ECO [kWh] | Real | Read | HoldingRegister | 2822 | kWh
2954 | RecHeat_PowerTemp_kWh | ECO [kWh] | Real | Read | HoldingRegister | 2824 | kWh
2955 | RecCool_PowerTemp_kWh | ECO [kW] | Real | Read | HoldingRegister | 2826 | kW
2956 | Heat_PowerTemp_kWh | ECO [kWh] | Real | Read | HoldingRegister | 2828 | kWh
2957 | Cool_PowerTemp_kWh | ECO [kW] | Real | Read | HoldingRegister | 2830 | kW
2958 | Recovery_Efficency | ECO [kWh] | Real | Read | HoldingRegister | 2832 | kWh
2959 | HC_Cool_1.Hrs | CT - Counter - Cooling - Device 1 [h] | UDInt | Read | HoldingRegister | 2834 | h | 0 - 999999
2960 | HC_Cool_2.Hrs | CT - Counter - Cooling - Device 2 [h] | UDInt | Read | HoldingRegister | 2836 | h | 0 - 999999
2961 | HC_ExhFan_1.Hrs | CT - Counter - Fan - Return 1 [h] | UDInt | Read | HoldingRegister | 2838 | h | 0 - 999999
2962 | HC_ExhFan_2.Hrs | CT - Counter - Fan - Return 2 [h] | UDInt | Read | HoldingRegister | 2840 | h | 0 - 999999
2963 | HC_Heat_1.Hrs | CT - Counter - Heating - Device 1 [h] | UDInt | Read | HoldingRegister | 2842 | h | 0 - 999999
2964 | HC_Heat_2.Hrs | CT - Counter - Heating - Device 2 [h] | UDInt | Read | HoldingRegister | 2844 | h | 0 - 999999
2965 | HC_Heat_Mod.Hrs | CT - Counter - Heating - Modulation [h] | UDInt | Read | HoldingRegister | 2846 | h | 0 - 999999
2966 | HC_Hum.Hrs | CT - Counter - Humidity [h] | UDInt | Read | HoldingRegister | 2848 | h | 0 - 999999
2967 | HC_PreHeat.Hrs | CT - Counter - PreHeating [h] | UDInt | Read | HoldingRegister | 2850 | h | 0 - 999999
2968 | HC_RecoveryPump.Hrs | CT - Counter - Recovery [h] | UDInt | Read | HoldingRegister | 2852 | h | 0 - 999999
2969 | HC_ReHeat.Hrs | CT - Counter - ReHeating [h] | UDInt | Read | HoldingRegister | 2854 | h | 0 - 999999
2970 | HC_SupplyFan_1.Hrs | CT - Counter - Fan - Supply 1 [h] | UDInt | Read | HoldingRegister | 2856 | h | 0 - 999999
2971 | HC_SupplyFan_2.Hrs | CT - Counter - Fan - Supply 2 [h] | UDInt | Read | HoldingRegister | 2858 | h | 0 - 999999
2972 | HC_Filter |  | UDInt |  | HoldingRegister | 2860
2973 | HC_Filter_Limit |  | UDInt |  | HoldingRegister | 2862
2974 | HC_SupplyFan_1.HrsRet |  | UDInt |  | HoldingRegister | 2864
2975 | HC_ExhFan_1.HrsRet |  | UDInt |  | HoldingRegister | 2866
2976 | HC_Heat_1.HrsRet |  | UDInt |  | HoldingRegister | 2868
2977 | HC_Cool_1.HrsRet |  | UDInt |  | HoldingRegister | 2870
2978 | HC_Heat_2.HrsRet |  | UDInt |  | HoldingRegister | 2872
2979 | HC_Cool_2.HrsRet |  | UDInt |  | HoldingRegister | 2874
2980 | HC_ReHeat.HrsRet |  | UDInt |  | HoldingRegister | 2876
2981 | HC_RecoveryPump.HrsRet |  | UDInt |  | HoldingRegister | 2878
2982 | HC_PreHeat.HrsRet |  | UDInt |  | HoldingRegister | 2880
2983 | HC_Hum.HrsRet |  | UDInt |  | HoldingRegister | 2882
2984 | MB_PressSupply_Adr |  | UDInt |  | HoldingRegister | 2884
2985 | MB_PressSupply_Adr_2 |  | UDInt |  | HoldingRegister | 2886
2986 | MB_PressSupply_Adr_3 |  | UDInt |  | HoldingRegister | 2888
2987 | MB_Devices.IO_PCB_1.AO1 |  | Real |  | HoldingRegister | 2890
2988 | MB_Devices.IO_PCB_1.AO2 |  | Real |  | HoldingRegister | 2892
2989 | MB_Devices.IO_PCB_1.AI1 |  | Real |  | HoldingRegister | 2894
2990 | MB_Set_Test |  | UInt |  | HoldingRegister | 2896
2991 | MB_Set_IRMS_Read |  | Int |  | HoldingRegister | 2897
2992 | MB_Set_FW_Read |  | Int |  | HoldingRegister | 2898
2993 | MB_Set_Error_Read |  | Int |  | HoldingRegister | 2899
2994 | MB_Set_Direct_Read |  | Int |  | HoldingRegister | 2900
2995 | MB_Set_Detect_Read |  | Int |  | HoldingRegister | 2901
2996 | MB_Set_Detect |  | Int |  | HoldingRegister | 2902
2997 | MB_Set_Addr |  | Int |  | HoldingRegister | 2903
2998 | MB_Set_Addr_New |  | Int |  | HoldingRegister | 2904
2999 | MB_Set_Addr_Read |  | Int |  | HoldingRegister | 2905
3000 | MB_Set_Addr_Old |  | Int |  | HoldingRegister | 2906
3001 | MB_Set_Case |  | USInt |  | HoldingRegister | 2907
3002 | MB_Set_MaxRPM |  | Int |  | HoldingRegister | 2908
3003 | MB_Set_MaxRPM_Read |  | Int |  | HoldingRegister | 2909
3004 | MB_Set_MinRPM_Read |  | Int |  | HoldingRegister | 2910
3005 | MB_Set_Mode |  | Int |  | HoldingRegister | 2911
3006 | MB_Set_Mode_Read |  | Int |  | HoldingRegister | 2912
3007 | MB_Set_Power_Read |  | Int |  | HoldingRegister | 2913
3008 | MB_Set_Speed_Read |  | Int |  | HoldingRegister | 2914
3009 | MB_PressReturn_Adr |  | UDInt |  | HoldingRegister | 2915
3010 | MB_PressReturn_Adr_2 |  | UDInt |  | HoldingRegister | 2917
3011 | MB_Press_FilterSup |  | Real |  | HoldingRegister | 2919
3012 | MB_Press_FilterRet |  | Real |  | HoldingRegister | 2921
3013 | UnitSetP_AirFlwSetP_StandBy |  | Real |  | HoldingRegister | 2923
3014 | UnitSetP_AirFlwSetP_StandBy_2 |  | Real |  | HoldingRegister | 2925
3015 | UnitSetP.RoomTempSetP.StandBy |  | Real |  | HoldingRegister | 2927
3016 | UnitSetP.HumSetP.StandBy |  | Real |  | HoldingRegister | 2929
3017 | UnitSetP.AirQualitySetP.StandBy |  | Real |  | HoldingRegister | 2931
3018 | UnitSetP.AirFlwSetP.StandBy |  | Real |  | HoldingRegister | 2933
3019 | UnitSetP.RetAirFlwSetP.StandBy |  | Real |  | HoldingRegister | 2935
3020 | PID_PreHeatCoil.SetP |  | Real |  | HoldingRegister | 2937
3021 | VAV_SupplySet |  | Real |  | HoldingRegister | 2939
3022 | CAV_SupplySet |  | Real |  | HoldingRegister | 2941
3023 | VAV_RetSet |  | Real |  | HoldingRegister | 2943
3024 | CAV_RetSet |  | Real |  | HoldingRegister | 2945
3025 | VAV_SupplyPID_Out |  | Real |  | HoldingRegister | 2947
3026 | VAV_ExhPID_Out |  | Real |  | HoldingRegister | 2949
3027 | CAV_SupplyPID_Out |  | Real |  | HoldingRegister | 2951
3028 | CAV_ExhPID_Out |  | Real |  | HoldingRegister | 2953
3029 | Heat_1.Man |  | USInt |  | HoldingRegister | 2955
3030 | SupplyAirFlow_2 |  | Int |  | HoldingRegister | 2956
3031 | ExhAirFlow_2 |  | Int |  | HoldingRegister | 2957
3032 | SupplyAirFlowSet_2 |  | Int |  | HoldingRegister | 2958
3033 | ExhAirFlowSet_2 |  | Int |  | HoldingRegister | 2959
3034 | SupplyTempSetP_RetComp |  | Real |  | HoldingRegister | 2960
3035 | Remote_Mode |  | Int |  | HoldingRegister | 2962
3036 | Pres_Filtr_Val |  | Real |  | HoldingRegister | 2963
3037 | SupHum_Offset |  | Real |  | HoldingRegister | 2965
3038 | RetHum_Offset |  | Real |  | HoldingRegister | 2967
3039 | CO2_Offset |  | Real |  | HoldingRegister | 2969
3040 | Typ_FP_Pressure |  | USInt |  | HoldingRegister | 2971
3041 | MainCoolMax |  | Real |  | HoldingRegister | 2972
3042 | ExhAirDamp.Man |  | USInt |  | HoldingRegister | 2974
3043 | ReturnDewPoint |  | Real |  | HoldingRegister | 2975
3044 | ExtTemp_Rec_En |  | Real |  | HoldingRegister | 2977
3045 | FanRecFrost |  | Real |  | HoldingRegister | 2979
3046 | FanRecFrost_Exh |  | Real |  | HoldingRegister | 2981
3047 | FanFlowAlarm_Delay | PAR - Fan - Supply - Warning Threshold Pressure delay [sec.] | DInt | ReadWrite | HoldingRegister | 2983 | sec.
3048 | RRG_Alarm_Delay | PAR - Recovery - Rotery - Dlarm delay [sec.] | DInt | ReadWrite | HoldingRegister | 2985 | sec.
3049 | BMS_Baud_msk |  | Int |  | HoldingRegister | 2987
3050 | pLan_Modbus |  | UInt |  | HoldingRegister | 2988
3051 | HMI_Alarm_code |  | Int |  | HoldingRegister | 2989
3052 | TempRegSetP |  | Real |  | HoldingRegister | 2990
3053 | Setpoint_Fan_Offset |  | Real |  | HoldingRegister | 2992
3054 | AHU_Status |  | Int |  | HoldingRegister | 2994
3055 | Setpoint_Temp_Offset |  | Real |  | HoldingRegister | 2995
3056 | EffectiveTempSetpoint |  | Real |  | HoldingRegister | 2997
3057 | SupplyFan_1.Current | MO - Fan - Supply 1 - Current [A] | Real | Read | HoldingRegister | 3001 | A
3058 | SupplyFan_1.DriveTemp | MO - Fan - Supply 1 - Drive temperature [°C] | Real | Read | HoldingRegister | 3003 | °C | USA
3059 | SupplyFan_1.Freq | MO - Fan - Supply 1 - Frequence [Hz] | Real | Read | HoldingRegister | 3005 | Hz
3060 | SupplyFan_1.kWh | MO - Fan - Supply 1 - Consumption [kWh] | Real | Read | HoldingRegister | 3007 | kWh | USA
3061 | SupplyFan_1.Power | MO - Fan - Supply 1 - Power [W] | Real | Read | HoldingRegister | 3009 | W
3062 | SupplyFan_1.Rpm | MO - Fan - Supply 1 - Speed [RPM] | Real | Read | HoldingRegister | 3011 | RPM
3063 | SupplyFan_1.Voltage | MO - Fan - Supply 1 - Voltage [V] | Real | Read | HoldingRegister | 3013 | V
3064 | MB_FanSupply_Adr_1 | Fan modbus address | UDInt | Read | HoldingRegister | 3015
3882 | SupplyFan_1.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3017
3883 | SupplyFan_1.OperDays | Fan operation days | Int | Read | HoldingRegister | 3018
3884 | MB_Devices.VFD_1.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3019
3065 | SupplyFan_2.Current | MO - Fan - Supply 2 - Current [A] | Real | Read | HoldingRegister | 3021 | A
3066 | SupplyFan_2.DriveTemp | MO - Fan - Supply 2 - Drive temperature [°C] | Real | Read | HoldingRegister | 3023 | °C | USA
3067 | SupplyFan_2.Freq | MO - Fan - Supply 2 - Frequence [Hz] | Real | Read | HoldingRegister | 3025 | Hz
3068 | SupplyFan_2.kWh | MO - Fan - Supply 2 - Consumption [kWh] | Real | Read | HoldingRegister | 3027 | kWh | USA
3069 | SupplyFan_2.Power | MO - Fan - Supply 2 - Power [W] | Real | Read | HoldingRegister | 3029 | W
3070 | SupplyFan_2.Rpm | MO - Fan - Supply 2 - Speed [RPM] | Real | Read | HoldingRegister | 3031 | RPM
3071 | SupplyFan_2.Voltage | MO - Fan - Supply 2 - Voltage [V] | Real | Read | HoldingRegister | 3033 | V
3072 | MB_FanSupply_Adr_2 | Fan modbus address | UDInt | Read | HoldingRegister | 3035
3885 | SupplyFan_2.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3037
3886 | SupplyFan_2.OperDays | Fan operation days | Int | Read | HoldingRegister | 3038
3887 | MB_Devices.VFD_2.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3039
3073 | SupplyFan_3.Current | MO - Fan - Supply 3 - Current [A] | Real | Read | HoldingRegister | 3041 | A
3074 | SupplyFan_3.DriveTemp | MO - Fan - Supply 3 - Drive temperature [°C] | Real | Read | HoldingRegister | 3043 | °C | USA
3075 | SupplyFan_3.Freq | MO - Fan - Supply 3 - Frequence [Hz] | Real | Read | HoldingRegister | 3045 | Hz
3076 | SupplyFan_3.kWh | MO - Fan - Supply 3 - Consumption [kWh] | Real | Read | HoldingRegister | 3047 | kWh | USA
3077 | SupplyFan_3.Power | MO - Fan - Supply 3 - Power [W] | Real | Read | HoldingRegister | 3049 | W
3078 | SupplyFan_3.Rpm | MO - Fan - Supply 3 - Speed [RPM] | Real | Read | HoldingRegister | 3051 | RPM
3079 | SupplyFan_3.Voltage | MO - Fan - Supply 3 - Voltage [V] | Real | Read | HoldingRegister | 3053 | V
3080 | MB_FanSupply_Adr_3 | Fan modbus address | UDInt | Read | HoldingRegister | 3055
3888 | SupplyFan_3.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3057
3889 | SupplyFan_3.OperDays | Fan operation days | Int | Read | HoldingRegister | 3058
3890 | MB_Devices.VFD_3.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3059
3081 | SupplyFan_4.Current | MO - Fan - Supply 4 - Current [A] | Real | Read | HoldingRegister | 3061 | A
3082 | SupplyFan_4.DriveTemp | MO - Fan - Supply 4 - Drive temperature [°C] | Real | Read | HoldingRegister | 3063 | °C | USA
3083 | SupplyFan_4.Freq | MO - Fan - Supply 4 - Frequence [Hz] | Real | Read | HoldingRegister | 3065 | Hz
3084 | SupplyFan_4.kWh | MO - Fan - Supply 4 - Consumption [kWh] | Real | Read | HoldingRegister | 3067 | kWh | USA
3085 | SupplyFan_4.Power | MO - Fan - Supply 4 - Power [W] | Real | Read | HoldingRegister | 3069 | W
3086 | SupplyFan_4.Rpm | MO - Fan - Supply 4 - Speed [RPM] | Real | Read | HoldingRegister | 3071 | RPM
3087 | SupplyFan_4.Voltage | MO - Fan - Supply 4 - Voltage [V] | Real | Read | HoldingRegister | 3073 | V
3088 | MB_FanSupply_Adr_4 | Fan modbus address | UDInt | Read | HoldingRegister | 3075
3891 | SupplyFan_4.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3077
3892 | SupplyFan_4.OperDays | Fan operation days | Int | Read | HoldingRegister | 3078
3893 | MB_Devices.VFD_4.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3079
3089 | SupplyFan_5.Current | MO - Fan - Supply 5 - Current [A] | Real | Read | HoldingRegister | 3081 | A
3090 | SupplyFan_5.DriveTemp | MO - Fan - Supply 5 - Drive temperature [°C] | Real | Read | HoldingRegister | 3083 | °C | USA
3091 | SupplyFan_5.Freq | MO - Fan - Supply 5 - Frequence [Hz] | Real | Read | HoldingRegister | 3085 | Hz
3092 | SupplyFan_5.kWh | MO - Fan - Supply 5 - Consumption [kWh] | Real | Read | HoldingRegister | 3087 | kWh | USA
3093 | SupplyFan_5.Power | MO - Fan - Supply 5 - Power [W] | Real | Read | HoldingRegister | 3089 | W
3094 | SupplyFan_5.Rpm | MO - Fan - Supply 5 - Speed [RPM] | Real | Read | HoldingRegister | 3091 | RPM
3095 | SupplyFan_5.Voltage | MO - Fan - Supply 5 - Voltage [V] | Real | Read | HoldingRegister | 3093 | V
3096 | MB_FanSupply_Adr_5 | Fan modbus address | UDInt | Read | HoldingRegister | 3095
3894 | SupplyFan_5.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3097
3895 | SupplyFan_5.OperDays | Fan operation days | Int | Read | HoldingRegister | 3098
3896 | MB_Devices.VFD_5.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3099
3097 | SupplyFan_6.Current | MO - Fan - Supply 6 - Current [A] | Real | Read | HoldingRegister | 3101 | A
3098 | SupplyFan_6.DriveTemp | MO - Fan - Supply 6 - Drive temperature [°C] | Real | Read | HoldingRegister | 3103 | °C | USA
3099 | SupplyFan_6.Freq | MO - Fan - Supply 6 - Frequence [Hz] | Real | Read | HoldingRegister | 3105 | Hz
3100 | SupplyFan_6.kWh | MO - Fan - Supply 6 - Consumption [kWh] | Real | Read | HoldingRegister | 3107 | kWh | USA
3101 | SupplyFan_6.Power | MO - Fan - Supply 6 - Power [W] | Real | Read | HoldingRegister | 3109 | W
3102 | SupplyFan_6.Rpm | MO - Fan - Supply 6 - Speed [RPM] | Real | Read | HoldingRegister | 3111 | RPM
3103 | SupplyFan_6.Voltage | MO - Fan - Supply 6 - Voltage [V] | Real | Read | HoldingRegister | 3113 | V
3104 | MB_FanSupply_Adr_6 | Fan modbus address | UDInt | Read | HoldingRegister | 3115
3897 | SupplyFan_6.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3117
3898 | SupplyFan_6.OperDays | Fan operation days | Int | Read | HoldingRegister | 3118
3899 | MB_Devices.VFD_12.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3119
3105 | SupplyFan_7.Current | MO - Fan - Supply 7 - Current [A] | Real | Read | HoldingRegister | 3121 | A
3106 | SupplyFan_7.DriveTemp | MO - Fan - Supply 7 - Drive temperature [°C] | Real | Read | HoldingRegister | 3123 | °C | USA
3107 | SupplyFan_7.Freq | MO - Fan - Supply 7 - Frequence [Hz] | Real | Read | HoldingRegister | 3125 | Hz
3108 | SupplyFan_7.kWh | MO - Fan - Supply 7 - Consumption [kWh] | Real | Read | HoldingRegister | 3127 | kWh | USA
3109 | SupplyFan_7.Power | MO - Fan - Supply 7 - Power [W] | Real | Read | HoldingRegister | 3129 | W
3110 | SupplyFan_7.Rpm | MO - Fan - Supply 7 - Speed [RPM] | Real | Read | HoldingRegister | 3131 | RPM
3111 | SupplyFan_7.Voltage | MO - Fan - Supply 7 - Voltage [V] | Real | Read | HoldingRegister | 3133 | V
3112 | MB_FanSupply_Adr_7 | Fan modbus address | UDInt | Read | HoldingRegister | 3135
3900 | SupplyFan_7.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3137
3901 | SupplyFan_7.OperDays | Fan operation days | Int | Read | HoldingRegister | 3138
3902 | MB_Devices.VFD_13.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3139
3113 | SupplyFan_8.Current | MO - Fan - Supply 8 - Current [A] | Real | Read | HoldingRegister | 3141 | A
3114 | SupplyFan_8.DriveTemp | MO - Fan - Supply 8 - Drive temperature [°C] | Real | Read | HoldingRegister | 3143 | °C | USA
3115 | SupplyFan_8.Freq | MO - Fan - Supply 8 - Frequence [Hz] | Real | Read | HoldingRegister | 3145 | Hz
3116 | SupplyFan_8.kWh | MO - Fan - Supply 8 - Consumption [kWh] | Real | Read | HoldingRegister | 3147 | kWh | USA
3117 | SupplyFan_8.Power | MO - Fan - Supply 8 - Power [W] | Real | Read | HoldingRegister | 3149 | W
3118 | SupplyFan_8.Rpm | MO - Fan - Supply 8 - Speed [RPM] | Real | Read | HoldingRegister | 3151 | RPM
3119 | SupplyFan_8.Voltage | MO - Fan - Supply 8 - Voltage [V] | Real | Read | HoldingRegister | 3153 | V
3120 | MB_FanSupply_Adr_8 | Fan modbus address | UDInt | Read | HoldingRegister | 3155
3903 | SupplyFan_8.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3157
3904 | SupplyFan_8.OperDays | Fan operation days | Int | Read | HoldingRegister | 3158
3905 | MB_Devices.VFD_14.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3159
3121 | SupplyFan_9.Current | MO - Fan - Supply 9 - Current [A] | Real | Read | HoldingRegister | 3161 | A
3122 | SupplyFan_9.DriveTemp | MO - Fan - Supply 9 - Drive temperature [°C] | Real | Read | HoldingRegister | 3163 | °C | USA
3123 | SupplyFan_9.Freq | MO - Fan - Supply 9 - Frequence [Hz] | Real | Read | HoldingRegister | 3165 | Hz
3124 | SupplyFan_9.kWh | MO - Fan - Supply 9 - Consumption [kWh] | Real | Read | HoldingRegister | 3167 | kWh | USA
3125 | SupplyFan_9.Power | MO - Fan - Supply 9 - Power [W] | Real | Read | HoldingRegister | 3169 | W
3126 | SupplyFan_9.Rpm | MO - Fan - Supply 9 - Speed [RPM] | Real | Read | HoldingRegister | 3171 | RPM
3127 | SupplyFan_9.Voltage | MO - Fan - Supply 9 - Voltage [V] | Real | Read | HoldingRegister | 3173 | V
3128 | MB_FanSupply_Adr_9 | Fan modbus address | UDInt | Read | HoldingRegister | 3175
3906 | SupplyFan_9.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3177
3907 | SupplyFan_9.OperDays | Fan operation days | Int | Read | HoldingRegister | 3178
3908 | MB_Devices.VFD_15.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3179
3129 | SupplyFan_10.Current | MO - Fan - Supply 10 - Current [A] | Real | Read | HoldingRegister | 3181 | A
3130 | SupplyFan_10.DriveTemp | MO - Fan - Supply 10 - Drive temperature [°C] | Real | Read | HoldingRegister | 3183 | °C | USA
3131 | SupplyFan_10.Freq | MO - Fan - Supply 10 - Frequence [Hz] | Real | Read | HoldingRegister | 3185 | Hz
3132 | SupplyFan_10.kWh | MO - Fan - Supply 10 - Consumption [kWh] | Real | Read | HoldingRegister | 3187 | kWh | USA
3133 | SupplyFan_10.Power | MO - Fan - Supply 10 - Power [W] | Real | Read | HoldingRegister | 3189 | W
3134 | SupplyFan_10.Rpm | MO - Fan - Supply 10 - Speed [RPM] | Real | Read | HoldingRegister | 3191 | RPM
3135 | SupplyFan_10.Voltage | MO - Fan - Supply 10 - Voltage [V] | Real | Read | HoldingRegister | 3193 | V
3136 | MB_FanSupply_Adr_10 | Fan modbus address | UDInt | Read | HoldingRegister | 3195
3909 | SupplyFan_10.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3197
3910 | SupplyFan_10.OperDays | Fan operation days | Int | Read | HoldingRegister | 3198
3911 | MB_Devices.VFD_16.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3199
3137 | SupplyFan_11.Current | MO - Fan - Supply 11 - Current [A] | Real | Read | HoldingRegister | 3201 | A
3138 | SupplyFan_11.DriveTemp | MO - Fan - Supply 11 - Drive temperature [°C] | Real | Read | HoldingRegister | 3203 | °C | USA
3139 | SupplyFan_11.Freq | MO - Fan - Supply 11 - Frequence [Hz] | Real | Read | HoldingRegister | 3205 | Hz
3140 | SupplyFan_11.kWh | MO - Fan - Supply 11 - Consumption [kWh] | Real | Read | HoldingRegister | 3207 | kWh | USA
3141 | SupplyFan_11.Power | MO - Fan - Supply 11 - Power [W] | Real | Read | HoldingRegister | 3209 | W
3142 | SupplyFan_11.Rpm | MO - Fan - Supply 11 - Speed [RPM] | Real | Read | HoldingRegister | 3211 | RPM
3143 | SupplyFan_11.Voltage | MO - Fan - Supply 11 - Voltage [V] | Real | Read | HoldingRegister | 3213 | V
3144 | MB_FanSupply_Adr_11 | Fan modbus address | UDInt | Read | HoldingRegister | 3215
3912 | SupplyFan_11.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3217
3913 | SupplyFan_11.OperDays | Fan operation days | Int | Read | HoldingRegister | 3218
3914 | MB_Devices.VFD_22.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3219
3145 | SupplyFan_12.Current | MO - Fan - Supply 12 - Current [A] | Real | Read | HoldingRegister | 3221 | A
3146 | SupplyFan_12.DriveTemp | MO - Fan - Supply 12 - Drive temperature [°C] | Real | Read | HoldingRegister | 3223 | °C | USA
3147 | SupplyFan_12.Freq | MO - Fan - Supply 12 - Frequence [Hz] | Real | Read | HoldingRegister | 3225 | Hz
3148 | SupplyFan_12.kWh | MO - Fan - Supply 12 - Consumption [kWh] | Real | Read | HoldingRegister | 3227 | kWh | USA
3149 | SupplyFan_12.Power | MO - Fan - Supply 12 - Power [W] | Real | Read | HoldingRegister | 3229 | W
3150 | SupplyFan_12.Rpm | MO - Fan - Supply 12 - Speed [RPM] | Real | Read | HoldingRegister | 3231 | RPM
3151 | SupplyFan_12.Voltage | MO - Fan - Supply 12 - Voltage [V] | Real | Read | HoldingRegister | 3233 | V
3152 | MB_FanSupply_Adr_12 | Fan modbus address | UDInt | Read | HoldingRegister | 3235
3915 | SupplyFan_12.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3237
3916 | SupplyFan_12.OperDays | Fan operation days | Int | Read | HoldingRegister | 3238
3917 | MB_Devices.VFD_23.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3239
3153 | SupplyFan_13.Current | MO - Fan - Supply 13 - Current [A] | Real | Read | HoldingRegister | 3241 | A
3154 | SupplyFan_13.DriveTemp | MO - Fan - Supply 13 - Drive temperature [°C] | Real | Read | HoldingRegister | 3243 | °C | USA
3155 | SupplyFan_13.Freq | MO - Fan - Supply 13 - Frequence [Hz] | Real | Read | HoldingRegister | 3245 | Hz
3156 | SupplyFan_13.kWh | MO - Fan - Supply 13 - Consumption [kWh] | Real | Read | HoldingRegister | 3247 | kWh | USA
3157 | SupplyFan_13.Power | MO - Fan - Supply 13 - Power [W] | Real | Read | HoldingRegister | 3249 | W
3158 | SupplyFan_13.Rpm | MO - Fan - Supply 13 - Speed [RPM] | Real | Read | HoldingRegister | 3251 | RPM
3159 | SupplyFan_13.Voltage | MO - Fan - Supply 13 - Voltage [V] | Real | Read | HoldingRegister | 3253 | V
3160 | MB_FanSupply_Adr_13 | Fan modbus address | UDInt | Read | HoldingRegister | 3255
3918 | SupplyFan_13.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3257
3919 | SupplyFan_13.OperDays | Fan operation days | Int | Read | HoldingRegister | 3258
3920 | MB_Devices.VFD_24.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3259
3161 | SupplyFan_14.Current | MO - Fan - Supply 14 - Current [A] | Real | Read | HoldingRegister | 3261 | A
3162 | SupplyFan_14.DriveTemp | MO - Fan - Supply 14 - Drive temperature [°C] | Real | Read | HoldingRegister | 3263 | °C | USA
3163 | SupplyFan_14.Freq | MO - Fan - Supply 14 - Frequence [Hz] | Real | Read | HoldingRegister | 3265 | Hz
3164 | SupplyFan_14.kWh | MO - Fan - Supply 14 - Consumption [kWh] | Real | Read | HoldingRegister | 3267 | kWh | USA
3165 | SupplyFan_14.Power | MO - Fan - Supply 14 - Power [W] | Real | Read | HoldingRegister | 3269 | W
3166 | SupplyFan_14.Rpm | MO - Fan - Supply 14 - Speed [RPM] | Real | Read | HoldingRegister | 3271 | RPM
3167 | SupplyFan_14.Voltage | MO - Fan - Supply 14 - Voltage [V] | Real | Read | HoldingRegister | 3273 | V
3168 | MB_FanSupply_Adr_14 | Fan modbus address | UDInt | Read | HoldingRegister | 3275
3921 | SupplyFan_14.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3277
3922 | SupplyFan_14.OperDays | Fan operation days | Int | Read | HoldingRegister | 3278
3923 | MB_Devices.VFD_25.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3279
3169 | SupplyFan_15.Current | MO - Fan - Supply 15 - Current [A] | Real | Read | HoldingRegister | 3281 | A
3170 | SupplyFan_15.DriveTemp | MO - Fan - Supply 15 - Drive temperature [°C] | Real | Read | HoldingRegister | 3283 | °C | USA
3171 | SupplyFan_15.Freq | MO - Fan - Supply 15 - Frequence [Hz] | Real | Read | HoldingRegister | 3285 | Hz
3172 | SupplyFan_15.kWh | MO - Fan - Supply 15 - Consumption [kWh] | Real | Read | HoldingRegister | 3287 | kWh | USA
3173 | SupplyFan_15.Power | MO - Fan - Supply 15 - Power [W] | Real | Read | HoldingRegister | 3289 | W
3174 | SupplyFan_15.Rpm | MO - Fan - Supply 15 - Speed [RPM] | Real | Read | HoldingRegister | 3291 | RPM
3175 | SupplyFan_15.Voltage | MO - Fan - Supply 15 - Voltage [V] | Real | Read | HoldingRegister | 3293 | V
3176 | MB_FanSupply_Adr_15 | Fan modbus address | UDInt | Read | HoldingRegister | 3295
3924 | SupplyFan_15.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3297
3925 | SupplyFan_15.OperDays | Fan operation days | Int | Read | HoldingRegister | 3298
3926 | MB_Devices.VFD_26.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3299
3177 | ExhFan_1.Current | MO - Fan - Return 1 - Current [A] | Real | Read | HoldingRegister | 3301 | A
3178 | ExhFan_1.DriveTemp | MO - Fan - Return 1 - Drive temperature [°C] | Real | Read | HoldingRegister | 3303 | °C | USA
3179 | ExhFan_1.Freq | MO - Fan - Return 1 - Frequence [Hz] | Real | Read | HoldingRegister | 3305 | Hz
3180 | ExhFan_1.kWh | MO - Fan - Return 1 - Consumption [kWh] | Real | Read | HoldingRegister | 3307 | kWh | USA
3181 | ExhFan_1.Power | MO - Fan - Return 1 - Power [W] | Real | Read | HoldingRegister | 3309 | W
3182 | ExhFan_1.Rpm | MO - Fan - Return 1 - Speed [RPM] | Real | Read | HoldingRegister | 3311 | RPM
3183 | ExhFan_1.Voltage | MO - Fan - Return 1 - Voltage [V] | Real | Read | HoldingRegister | 3313 | V
3184 | MB_FanReturn_Adr_1 | Fan modbus address | UDInt | Read | HoldingRegister | 3315
3927 | ExhFan_1.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3317
3928 | ExhFan_1.OperDays | Fan operation days | Int | Read | HoldingRegister | 3318
3929 | MB_Devices.VFD_6.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3319
3185 | ExhFan_2.Current | MO - Fan - Return 2 - Current [A] | Real | Read | HoldingRegister | 3321 | A
3186 | ExhFan_2.DriveTemp | MO - Fan - Return 2 - Drive temperature [°C] | Real | Read | HoldingRegister | 3323 | °C | USA
3187 | ExhFan_2.Freq | MO - Fan - Return 2 - Frequence [Hz] | Real | Read | HoldingRegister | 3325 | Hz
3188 | ExhFan_2.kWh | MO - Fan - Return 2 - Consumption [kWh] | Real | Read | HoldingRegister | 3327 | kWh | USA
3189 | ExhFan_2.Power | MO - Fan - Return 2 - Power [W] | Real | Read | HoldingRegister | 3329 | W
3190 | ExhFan_2.Rpm | MO - Fan - Return 2 - Speed [RPM] | Real | Read | HoldingRegister | 3331 | RPM
3191 | ExhFan_2.Voltage | MO - Fan - Return 2 - Voltage [V] | Real | Read | HoldingRegister | 3333 | V
3192 | MB_FanReturn_Adr_2 | Fan modbus address | UDInt |  | HoldingRegister | 3335
3930 | ExhFan_2.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3337
3931 | ExhFan_2.OperDays | Fan operation days | Int |  | HoldingRegister | 3338
3932 | MB_Devices.VFD_7.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3339
3193 | ExhFan_3.Current | MO - Fan - Return 3 - Current [A] | Real | Read | HoldingRegister | 3341 | A
3194 | ExhFan_3.DriveTemp | MO - Fan - Return 3 - Drive temperature [°C] | Real | Read | HoldingRegister | 3343 | °C | USA
3195 | ExhFan_3.Freq | MO - Fan - Return 3 - Frequence [Hz] | Real | Read | HoldingRegister | 3345 | Hz
3196 | ExhFan_3.kWh | MO - Fan - Return 3 - Consumption [kWh] | Real | Read | HoldingRegister | 3347 | kWh | USA
3197 | ExhFan_3.Power | MO - Fan - Return 3 - Power [W] | Real | Read | HoldingRegister | 3349 | W
3198 | ExhFan_3.Rpm | MO - Fan - Return 3 - Speed [RPM] | Real | Read | HoldingRegister | 3351 | RPM
3199 | ExhFan_3.Voltage | MO - Fan - Return 3 - Voltage [V] | Real | Read | HoldingRegister | 3353 | V
3200 | MB_FanReturn_Adr_3 | Fan modbus address | UDInt |  | HoldingRegister | 3355
3933 | ExhFan_3.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3357
3934 | ExhFan_3.OperDays | Fan operation days | Int |  | HoldingRegister | 3358
3935 | MB_Devices.VFD_8.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3359
3201 | ExhFan_4.Current | MO - Fan - Return 4 - Current [A] | Real | Read | HoldingRegister | 3361 | A
3202 | ExhFan_4.DriveTemp | MO - Fan - Return 4 - Drive temperature [°C] | Real | Read | HoldingRegister | 3363 | °C | USA
3203 | ExhFan_4.Freq | MO - Fan - Return 4 - Frequence [Hz] | Real | Read | HoldingRegister | 3365 | Hz
3204 | ExhFan_4.kWh | MO - Fan - Return 4 - Consumption [kWh] | Real | Read | HoldingRegister | 3367 | kWh | USA
3205 | ExhFan_4.Power | MO - Fan - Return 4 - Power [W] | Real | Read | HoldingRegister | 3369 | W
3206 | ExhFan_4.Rpm | MO - Fan - Return 4 - Speed [RPM] | Real | Read | HoldingRegister | 3371 | RPM
3207 | ExhFan_4.Voltage | MO - Fan - Return 4 - Voltage [V] | Real | Read | HoldingRegister | 3373 | V
3208 | MB_FanReturn_Adr_4 | Fan modbus address | UDInt |  | HoldingRegister | 3375
3936 | ExhFan_4.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3377
3937 | ExhFan_4.OperDays | Fan operation days | Int |  | HoldingRegister | 3378
3938 | MB_Devices.VFD_9.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3379
3209 | ExhFan_5.Current | MO - Fan - Return 5 - Current [A] | Real | Read | HoldingRegister | 3381 | A
3210 | ExhFan_5.DriveTemp | MO - Fan - Return 5 - Drive temperature [°C] | Real | Read | HoldingRegister | 3383 | °C | USA
3211 | ExhFan_5.Freq | MO - Fan - Return 5 - Frequence [Hz] | Real | Read | HoldingRegister | 3385 | Hz
3212 | ExhFan_5.kWh | MO - Fan - Return 5 - Consumption [kWh] | Real | Read | HoldingRegister | 3387 | kWh | USA
3213 | ExhFan_5.Power | MO - Fan - Return 5 - Power [W] | Real | Read | HoldingRegister | 3389 | W
3214 | ExhFan_5.Rpm | MO - Fan - Return 5 - Speed [RPM] | Real | Read | HoldingRegister | 3391 | RPM
3215 | ExhFan_5.Voltage | MO - Fan - Return 5 - Voltage [V] | Real | Read | HoldingRegister | 3393 | V
3216 | MB_FanReturn_Adr_5 | Fan modbus address | UDInt |  | HoldingRegister | 3395
3939 | ExhFan_5.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3397
3940 | ExhFan_5.OperDays | Fan operation days | Int |  | HoldingRegister | 3398
3941 | MB_Devices.VFD_10.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3399
3217 | ExhFan_6.Current | MO - Fan - Return 6 - Current [A] | Real | Read | HoldingRegister | 3401 | A
3218 | ExhFan_6.DriveTemp | MO - Fan - Return 6 - Drive temperature [°C] | Real | Read | HoldingRegister | 3403 | °C | USA
3219 | ExhFan_6.Freq | MO - Fan - Return 6 - Frequence [Hz] | Real | Read | HoldingRegister | 3405 | Hz
3220 | ExhFan_6.kWh | MO - Fan - Return 6 - Consumption [kWh] | Real | Read | HoldingRegister | 3407 | kWh | USA
3221 | ExhFan_6.Power | MO - Fan - Return 6 - Power [W] | Real | Read | HoldingRegister | 3409 | W
3222 | ExhFan_6.Rpm | MO - Fan - Return 6 - Speed [RPM] | Real | Read | HoldingRegister | 3411 | RPM
3223 | ExhFan_6.Voltage | MO - Fan - Return 6 - Voltage [V] | Real | Read | HoldingRegister | 3413 | V
3224 | MB_FanReturn_Adr_6 | Fan modbus address | UDInt |  | HoldingRegister | 3415
3942 | ExhFan_6.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3417
3943 | ExhFan_6.OperDays | Fan operation days | Int |  | HoldingRegister | 3418
3944 | MB_Devices.VFD_17.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3419
3225 | ExhFan_7.Current | MO - Fan - Return 7 - Current [A] | Real | Read | HoldingRegister | 3421 | A
3226 | ExhFan_7.DriveTemp | MO - Fan - Return 7 - Drive temperature [°C] | Real | Read | HoldingRegister | 3423 | °C | USA
3227 | ExhFan_7.Freq | MO - Fan - Return 7 - Frequence [Hz] | Real | Read | HoldingRegister | 3425 | Hz
3228 | ExhFan_7.kWh | MO - Fan - Return 7 - Consumption [kWh] | Real | Read | HoldingRegister | 3427 | kWh | USA
3229 | ExhFan_7.Power | MO - Fan - Return 7 - Power [W] | Real | Read | HoldingRegister | 3429 | W
3230 | ExhFan_7.Rpm | MO - Fan - Return 7 - Speed [RPM] | Real | Read | HoldingRegister | 3431 | RPM
3231 | ExhFan_7.Voltage | MO - Fan - Return 7 - Voltage [V] | Real | Read | HoldingRegister | 3433 | V
3232 | MB_FanReturn_Adr_7 | Fan modbus address | UDInt |  | HoldingRegister | 3435
3945 | ExhFan_7.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3437
3946 | ExhFan_7.OperDays | Fan operation days | Int |  | HoldingRegister | 3438
3947 | MB_Devices.VFD_18.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3439
3233 | ExhFan_8.Current | MO - Fan - Return 8 - Current [A] | Real | Read | HoldingRegister | 3441 | A
3234 | ExhFan_8.DriveTemp | MO - Fan - Return 8 - Drive temperature [°C] | Real | Read | HoldingRegister | 3443 | °C | USA
3235 | ExhFan_8.Freq | MO - Fan - Return 8 - Frequence [Hz] | Real | Read | HoldingRegister | 3445 | Hz
3236 | ExhFan_8.kWh | MO - Fan - Return 8 - Consumption [kWh] | Real | Read | HoldingRegister | 3447 | kWh | USA
3237 | ExhFan_8.Power | MO - Fan - Return 8 - Power [W] | Real | Read | HoldingRegister | 3449 | W
3238 | ExhFan_8.Rpm | MO - Fan - Return 8 - Speed [RPM] | Real | Read | HoldingRegister | 3451 | RPM
3239 | ExhFan_8.Voltage | MO - Fan - Return 8 - Voltage [V] | Real | Read | HoldingRegister | 3453 | V
3240 | MB_FanReturn_Adr_8 | Fan modbus address | UDInt |  | HoldingRegister | 3455
3948 | ExhFan_8.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3457
3949 | ExhFan_8.OperDays | Fan operation days | Int |  | HoldingRegister | 3458
3950 | MB_Devices.VFD_19.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3459
3241 | ExhFan_9.Current | MO - Fan - Return 9 - Current [A] | Real | Read | HoldingRegister | 3461 | A
3242 | ExhFan_9.DriveTemp | MO - Fan - Return 9 - Drive temperature [°C] | Real | Read | HoldingRegister | 3463 | °C | USA
3243 | ExhFan_9.Freq | MO - Fan - Return 9 - Frequence [Hz] | Real | Read | HoldingRegister | 3465 | Hz
3244 | ExhFan_9.kWh | MO - Fan - Return 9 - Consumption [kWh] | Real | Read | HoldingRegister | 3467 | kWh | USA
3245 | ExhFan_9.Power | MO - Fan - Return 9 - Power [W] | Real | Read | HoldingRegister | 3469 | W
3246 | ExhFan_9.Rpm | MO - Fan - Return 9 - Speed [RPM] | Real | Read | HoldingRegister | 3471 | RPM
3247 | ExhFan_9.Voltage | MO - Fan - Return 9 - Voltage [V] | Real | Read | HoldingRegister | 3473 | V
3248 | MB_FanReturn_Adr_9 | Fan modbus address | UDInt |  | HoldingRegister | 3475
3951 | ExhFan_9.OperMin | Fan operation miunutes | Int |  | HoldingRegister | 3477
3952 | ExhFan_9.OperDays | Fan operation days | Int |  | HoldingRegister | 3478
3953 | MB_Devices.VFD_20.Delay_AL | Fan alarm delay | UDInt |  | HoldingRegister | 3479
3249 | ExhFan_10.Current | MO - Fan - Return 10 - Current [A] | Real | Read | HoldingRegister | 3481 | A
3250 | ExhFan_10.DriveTemp | MO - Fan - Return 10 - Drive temperature [°C] | Real | Read | HoldingRegister | 3483 | °C | USA
3251 | ExhFan_10.Freq | MO - Fan - Return 10 - Frequence [Hz] | Real | Read | HoldingRegister | 3485 | Hz
3252 | ExhFan_10.kWh | MO - Fan - Return 10 - Consumption [kWh] | Real | Read | HoldingRegister | 3487 | kWh | USA
3253 | ExhFan_10.Power | MO - Fan - Return 10 - Power [W] | Real | Read | HoldingRegister | 3489 | W
3254 | ExhFan_10.Rpm | MO - Fan - Return 10 - Speed [RPM] | Real | Read | HoldingRegister | 3491 | RPM
3255 | ExhFan_10.Voltage | MO - Fan - Return 10 - Voltage [V] | Real | Read | HoldingRegister | 3493 | V
3256 | MB_FanReturn_Adr_10 | Fan modbus address | UDInt | Read | HoldingRegister | 3495
3954 | ExhFan_10.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3497
3955 | ExhFan_10.OperDays | Fan operation days | Int | Read | HoldingRegister | 3498
3956 | MB_Devices.VFD_21.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3499
3257 | ExhFan_11.Current | MO - Fan - Return 11 - Current [A] | Real | Read | HoldingRegister | 3501 | A
3258 | ExhFan_11.DriveTemp | MO - Fan - Return 11 - Drive temperature [°C] | Real | Read | HoldingRegister | 3503 | °C | USA
3259 | ExhFan_11.Freq | MO - Fan - Return 11 - Frequence [Hz] | Real | Read | HoldingRegister | 3505 | Hz
3260 | ExhFan_11.kWh | MO - Fan - Return 11 - Consumption [kWh] | Real | Read | HoldingRegister | 3507 | kWh | USA
3261 | ExhFan_11.Power | MO - Fan - Return 11 - Power [W] | Real | Read | HoldingRegister | 3509 | W
3262 | ExhFan_11.Rpm | MO - Fan - Return 11 - Speed [RPM] | Real | Read | HoldingRegister | 3511 | RPM
3263 | ExhFan_11.Voltage | MO - Fan - Return 11 - Voltage [V] | Real | Read | HoldingRegister | 3513 | V
3264 | MB_FanReturn_Adr_11 | Fan modbus address | UDInt | Read | HoldingRegister | 3515
3957 | ExhFan_11.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3517
3958 | ExhFan_11.OperDays | Fan operation days | Int | Read | HoldingRegister | 3518
3959 | MB_Devices.VFD_27.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3519
3265 | ExhFan_12.Current | MO - Fan - Return 12 - Current [A] | Real | Read | HoldingRegister | 3521 | A
3266 | ExhFan_12.DriveTemp | MO - Fan - Return 12 - Drive temperature [°C] | Real | Read | HoldingRegister | 3523 | °C | USA
3267 | ExhFan_12.Freq | MO - Fan - Return 12 - Frequence [Hz] | Real | Read | HoldingRegister | 3525 | Hz
3268 | ExhFan_12.kWh | MO - Fan - Return 12 - Consumption [kWh] | Real | Read | HoldingRegister | 3527 | kWh | USA
3269 | ExhFan_12.Power | MO - Fan - Return 12 - Power [W] | Real | Read | HoldingRegister | 3529 | W
3270 | ExhFan_12.Rpm | MO - Fan - Return 12 - Speed [RPM] | Real | Read | HoldingRegister | 3531 | RPM
3271 | ExhFan_12.Voltage | MO - Fan - Return 12 - Voltage [V] | Real | Read | HoldingRegister | 3533 | V
3272 | MB_FanReturn_Adr_12 | Fan modbus address | UDInt | Read | HoldingRegister | 3535
3960 | ExhFan_12.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3537
3961 | ExhFan_12.OperDays | Fan operation days | Int | Read | HoldingRegister | 3538
3962 | MB_Devices.VFD_28.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3539
3273 | ExhFan_13.Current | MO - Fan - Return 13 - Current [A] | Real | Read | HoldingRegister | 3541 | A
3274 | ExhFan_13.DriveTemp | MO - Fan - Return 13 - Drive temperature [°C] | Real | Read | HoldingRegister | 3543 | °C | USA
3275 | ExhFan_13.Freq | MO - Fan - Return 13 - Frequence [Hz] | Real | Read | HoldingRegister | 3545 | Hz
3276 | ExhFan_13.kWh | MO - Fan - Return 13 - Consumption [kWh] | Real | Read | HoldingRegister | 3547 | kWh | USA
3277 | ExhFan_13.Power | MO - Fan - Return 13 - Power [W] | Real | Read | HoldingRegister | 3549 | W
3278 | ExhFan_13.Rpm | MO - Fan - Return 13 - Speed [RPM] | Real | Read | HoldingRegister | 3551 | RPM
3279 | ExhFan_13.Voltage | MO - Fan - Return 13 - Voltage [V] | Real | Read | HoldingRegister | 3553 | V
3280 | MB_FanReturn_Adr_13 | Fan modbus address | UDInt | Read | HoldingRegister | 3555
3963 | ExhFan_13.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3557
3964 | ExhFan_13.OperDays | Fan operation days | Int | Read | HoldingRegister | 3558
3965 | MB_Devices.VFD_29.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3559
3281 | ExhFan_14.Current | MO - Fan - Return 14 - Current [A] | Real | Read | HoldingRegister | 3561 | A
3282 | ExhFan_14.DriveTemp | MO - Fan - Return 14 - Drive temperature [°C] | Real | Read | HoldingRegister | 3563 | °C | USA
3283 | ExhFan_14.Freq | MO - Fan - Return 14 - Frequence [Hz] | Real | Read | HoldingRegister | 3565 | Hz
3284 | ExhFan_14.kWh | MO - Fan - Return 14 - Consumption [kWh] | Real | Read | HoldingRegister | 3567 | kWh | USA
3285 | ExhFan_14.Power | MO - Fan - Return 14 - Power [W] | Real | Read | HoldingRegister | 3569 | W
3286 | ExhFan_14.Rpm | MO - Fan - Return 14 - Speed [RPM] | Real | Read | HoldingRegister | 3571 | RPM
3287 | ExhFan_14.Voltage | MO - Fan - Return 14 - Voltage [V] | Real | Read | HoldingRegister | 3573 | V
3288 | MB_FanReturn_Adr_14 | Fan modbus address | UDInt | Read | HoldingRegister | 3575
3966 | ExhFan_14.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3577
3967 | ExhFan_14.OperDays | Fan operation days | Int | Read | HoldingRegister | 3578
3968 | MB_Devices.VFD_30.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3579
3289 | ExhFan_15.Current | MO - Fan - Return 15 - Current [A] | Real | Read | HoldingRegister | 3581 | A
3290 | ExhFan_15.DriveTemp | MO - Fan - Return 15 - Drive temperature [°C] | Real | Read | HoldingRegister | 3583 | °C | USA
3291 | ExhFan_15.Freq | MO - Fan - Return 15 - Frequence [Hz] | Real | Read | HoldingRegister | 3585 | Hz
3292 | ExhFan_15.kWh | MO - Fan - Return 15 - Consumption [kWh] | Real | Read | HoldingRegister | 3587 | kWh | USA
3293 | ExhFan_15.Power | MO - Fan - Return 15 - Power [W] | Real | Read | HoldingRegister | 3589 | W
3294 | ExhFan_15.Rpm | MO - Fan - Return 15 - Speed [RPM] | Real | Read | HoldingRegister | 3591 | RPM
3295 | ExhFan_15.Voltage | MO - Fan - Return 15 - Voltage [V] | Real | Read | HoldingRegister | 3593 | V
3296 | MB_FanReturn_Adr_15 | Fan modbus address | UDInt | Read | HoldingRegister | 3595
3969 | ExhFan_15.OperMin | Fan operation miunutes | Int | Read | HoldingRegister | 3597
3970 | ExhFan_15.OperDays | Fan operation days | Int | Read | HoldingRegister | 3598
3971 | MB_Devices.VFD_31.Delay_AL | Fan alarm delay | UDInt | Read | HoldingRegister | 3599
3297 | VFD_SupChange_RPM |  | Int | Read | HoldingRegister | 3601
3298 | VFD_RetChange_RPM |  | Int | Read | HoldingRegister | 3602
3299 | MB_Devices.VFD_1.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3603
3300 | MB_Devices.VFD_2.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3604
3301 | MB_Devices.VFD_3.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3605
3302 | MB_Devices.VFD_4.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3606
3303 | MB_Devices.VFD_5.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3607
3304 | MB_Devices.VFD_6.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3608
3305 | MB_Devices.VFD_7.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3609
3306 | MB_Devices.VFD_8.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3610
3307 | MB_Devices.VFD_9.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3611
3308 | MB_Devices.VFD_10.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3612
3309 | MB_Devices.VFD_11.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3613
3310 | MB_Devices.VFD_12.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3614
3311 | MB_Devices.VFD_13.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3615
3312 | MB_Devices.VFD_14.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3616
3313 | MB_Devices.VFD_15.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3617
3314 | MB_Devices.VFD_16.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3618
3315 | MB_Devices.VFD_17.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3619
3316 | MB_Devices.VFD_18.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3620
3317 | MB_Devices.VFD_19.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3621
3318 | MB_Devices.VFD_20.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3622
3319 | MB_Devices.VFD_21.MBM_Params.MaxFreq |  | Int | Read | HoldingRegister | 3623
3320 | Rotary.Current | MO - Recovery - Rotary - Current [A] | Real | Read | HoldingRegister | 3624 | A
3321 | Rotary.DriveTemp | MO - Recovery - Rotary - Drive temperature [°C] | Real | Read | HoldingRegister | 3626 | °C | USA
3322 | Rotary.Freq | MO - Recovery - Rotary - Frequence [Hz] | Real | Read | HoldingRegister | 3628 | Hz
3323 | Rotary.kWh | MO - Recovery - Rotary - Consumption [kWh] | Real | Read | HoldingRegister | 3630 | kWh | USA
3324 | Rotary.Power | MO - Recovery - Rotary - Power [W] | Real | Read | HoldingRegister | 3632 | W
3325 | Rotary.Rpm | MO - Recovery - Rotary - Speed [RPM] | Real | Read | HoldingRegister | 3634 | RPM
3326 | Rotary.Voltage | MO - Recovery - Rotary - Voltage [V] | Real | Read | HoldingRegister | 3636 | V
3327 | SupplyFan_1_Power | MO - Fan - Supply - Power [W] | Real | Read | HoldingRegister | 3638 | W
3328 | SupplyFanVal | MO - Fan - Supply - Value [%] | Real | Read | HoldingRegister | 3640 | % | 0 - 100 %
3329 | ExhFan_1_Power | MO - Fan - Return - Power [W] | Real | Read | HoldingRegister | 3642 | W
3330 | ExhFanVal | MO - Fan - Return - Value [%] | Real | Read | HoldingRegister | 3644 | % | 0 - 100 %
3331 | SuppFanVal_Base |  | Real |  | HoldingRegister | 3646
3332 | ExhFanVal_Base |  | Real |  | HoldingRegister | 3648
3972 | MB_Devices.VFD_22.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3650
3973 | MB_Devices.VFD_23.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3652
3974 | MB_Devices.VFD_24.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3654
3975 | MB_Devices.VFD_25.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3656
3976 | MB_Devices.VFD_26.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3658
3977 | MB_Devices.VFD_27.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3660
3978 | MB_Devices.VFD_28.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3662
3979 | MB_Devices.VFD_29.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3664
3980 | MB_Devices.VFD_30.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3666
3981 | MB_Devices.VFD_31.MBM_Params.MaxFreq |  | Real |  | HoldingRegister | 3668
3333 | AfterPreHeatCoilTemp.Val | IO - Probe - Temperature - After PreHeat [°C] | Real | Read | HoldingRegister | 3701 | °C
3334 | Cool_Val_AO |  | Real |  | HoldingRegister | 3703
3335 | Reverse_Val_AO |  | Real |  | HoldingRegister | 3705
3336 | ExhAirFlow | IO - Probe - Air Flow - Return [m3/h] | Real | Read | HoldingRegister | 3707 | m3/h
3337 | ExhAirP_Val | IO - Probe - Pressure - Return [Pa] | Real | Read | HoldingRegister | 3709 | Pa
3338 | ExhTemp.Val | IO - Probe - Temperature - Recovery [°C] | Real | Read | HoldingRegister | 3711 | °C
3339 | ExtTemp.Val | IO - Probe - Temperature - External [°C] | Real | Read | HoldingRegister | 3713 | °C
3340 | HeatRecovery_Val | IO - Analog Output - Rotary - Value [%] | Real | Read | HoldingRegister | 3715 | % | 0 - 100 %
3341 | Heat_Val_AO |  | Real |  | HoldingRegister | 3717
3342 | MB_Devices.MB_MainBoard_1.AI_Temp_Fan_Return | IO - Module IO - Temperature Fan Return [°C] | Real | Read | HoldingRegister | 3719 | °C
3343 | MB_Devices.MB_MainBoard_1.AI_Temp_Fan_Supply | IO - Module IO - Temperature Fan Supply [°C] | Real | Read | HoldingRegister | 3721 | °C
3344 | MB_Devices.MB_MainBoard_1.AO_01_Read | IO - Module IO - Analog output 1 [%] | Real | Read | HoldingRegister | 3723 | %
3345 | MB_Devices.MB_MainBoard_1.AO_02_Read | IO - Module IO - Analog output 2 [%] | Real | Read | HoldingRegister | 3725 | %
3346 | MB_Devices.MB_MainBoard_1.AO_03_Read | IO - Module IO - Analog output 3 [%] | Real | Read | HoldingRegister | 3727 | %
3347 | MB_Devices.MB_MainBoard_1.AO_04_Read | IO - Module IO - Analog output 4 [%] | Real | Read | HoldingRegister | 3729 | %
3348 | MB_Devices.MB_MainBoard_1.Humid_Return | IO - Module IO - Humidity Return [%] | Real | Read | HoldingRegister | 3731 | %
3349 | MB_Devices.MB_MainBoard_1.Pressure_Fan_Return | IO - Module IO - Pressure Fan Return [Pa] | Real | Read | HoldingRegister | 3733 | Pa
3350 | MB_Devices.MB_MainBoard_1.Pressure_Fan_Supply | IO - Module IO - Pressure Fan Supply [Pa] | Real | Read | HoldingRegister | 3735 | Pa
3351 | MB_Devices.MB_MainBoard_1.Pressure_Filter_Return | IO - Module IO - Pressure Filter Return [Pa] | Real | Read | HoldingRegister | 3737 | Pa
3352 | MB_Devices.MB_MainBoard_1.Pressure_Filter_Supply | IO - Module IO - Pressure Filter Supply [Pa] | Real | Read | HoldingRegister | 3739 | Pa
3353 | MB_Devices.MB_MainBoard_1.Supply_24V_Read | IO - Module IO - Supply 24V [V] | Real | Read | HoldingRegister | 3741 | V
3354 | MB_Devices.MB_MainBoard_1.Supply_Control_Read | IO - Module IO - Supply Controller [V] | Real | Read | HoldingRegister | 3743 | V
3355 | MB_Devices.MB_MainBoard_1.Temp_Return | IO - Module IO - Temperature Return [°C] | Real | Read | HoldingRegister | 3745 | °C
3356 | MixDampReq_Fresh | IO - Analog Output - Damper - External [%] | Real | Read | HoldingRegister | 3747 | % | 0 - 100 %
3357 | Humid_Val_AO |  | Real |  | HoldingRegister | 3749
3358 | ModulMixDamp_Val | IO - Analog Output - Damper - Mixing [%] | Real | Read | HoldingRegister | 3751 | % | 0 - 100 %
3359 | PreHeat_Val_AO |  | Real |  | HoldingRegister | 3753
3360 | RecSupplyTemp.Val | IO - Probe - Temperature - Supply after recovery [°C] | Real | Read | HoldingRegister | 3755 | °C
3361 | ReHeat_Val_AO |  | Real |  | HoldingRegister | 3757
3362 | RetAir_CO2_Val | IO - Probe - CO2 - Return [ppm] | Real | Read | HoldingRegister | 3759 | ppm
3363 | RetHum_Val | IO - Probe - Humidity - Return [%] | Real | Read | HoldingRegister | 3761 | % | 0 - 100 %
3364 | RetTemp.Val | IO - Probe - Temperature - Return / Room [°C] | Real | Read | HoldingRegister | 3763 | °C
3365 | SupplyAirFlow | IO - Probe - Air Flow - Supply [m3/h] | Real | Read | HoldingRegister | 3765 | m3/h
3366 | SupplyAirP_Val | IO - Probe - Pressure - Supply [Pa] | Real | Read | HoldingRegister | 3767 | Pa
3367 | SupplyHum_Val | IO - Probe - Humidity - Supply [%] | Real | Read | HoldingRegister | 3769 | % | 0 - 100 %
3368 | SupplyTemp.Val | IO - Probe - Temperature - Supply [°C] | Real | Read | HoldingRegister | 3771 | °C
3369 | Temp_THTN_1 | IO - Probe - Temperature - TH Room [°C] | Real | Read | HoldingRegister | 3773 | °C
3370 | W_HeatCoilTemp.Val | IO - Probe - Temperature - Water Heat [°C] | Real | Read | HoldingRegister | 3775 | °C
3371 | W_PreHeatCoilTemp.Val | IO - Probe - Temperature - Water PreHeat [°C] | Real | Read | HoldingRegister | 3777 | °C
3372 | Y1Out_HW | IO - Analog Output - Y1 [%] | Real | Read | HoldingRegister | 3779 | % | 0 - 100 %
3373 | Y2Out_HW | IO - Analog Output - Y2 [%] | Real | Read | HoldingRegister | 3781 | % | 0 - 100 %
3374 | Y3Out_HW | IO - Analog Output - Y3 [%] | Real | Read | HoldingRegister | 3783 | % | 0 - 100 %
3375 | SupplyAirP_Val_2 |  | Real |  | HoldingRegister | 3785
3376 | SupplyAirP_Val_3 |  | Real |  | HoldingRegister | 3787
3377 | ExhAirP_Val_2 |  | Real |  | HoldingRegister | 3789
3378 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SH_Val | SuperHeat | Real |  | HoldingRegister | 3801 | K | Heat Pump cPCO variable
3379 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_rps | Current rotor speed [rps] | Real |  | HoldingRegister | 3803 |  | Heat Pump cPCO variable
3380 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_EEV_Pos%_Val | Valve opening | Real |  | HoldingRegister | 3805 | % | Heat Pump cPCO variable
3381 | PWRP_Info_MotA | Current motor current [A] | Real |  | HoldingRegister | 3807 |  | Heat Pump cPCO variable
3382 | UnitStatus | Unit staus | UInt |  | HoldingRegister | 3809 |  | Heat Pump cPCO variable
3383 | CompPwrReq | Compressor power request [%] | Real |  | HoldingRegister | 3811 | % | Heat Pump cPCO variable
3384 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_Perc | Current rotor speed [%] | Real |  | HoldingRegister | 3813 | % | Heat Pump cPCO variable
3385 | DscgP | Discharge pressure | Real |  | HoldingRegister | 3815 |  | Heat Pump cPCO variable
3386 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CondTemp_Val | Condensing temperature | Real |  | HoldingRegister | 3817 | °C | Heat Pump cPCO variable
3387 | DscgTemp | Discharge temperature | Real |  | HoldingRegister | 3819 |  | Heat Pump cPCO variable
3388 | SuctTemp | Suction temperature | Real |  | HoldingRegister | 3821 |  | Heat Pump cPCO variable
3389 | SuctP | Suction pressure | Real |  | HoldingRegister | 3823 |  | Heat Pump cPCO variable
3390 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SH_EvapTemp_Val | Evaporation temperature | Real |  | HoldingRegister | 3825 | °C | Heat Pump cPCO variable
3391 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val | Valve position | UInt |  | HoldingRegister | 3827 |  | Heat Pump cPCO variable
3392 | EEVSet | Suction SH set | Real |  | HoldingRegister | 3829 |  | Heat Pump cPCO variable
3393 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_DscgSH_Val | Discharge superheat | Real |  | HoldingRegister | 3831 | K | Heat Pump cPCO variable
3394 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_DriveStatus | Drive status | Int |  | HoldingRegister | 3833 |  | Heat Pump cPCO variable
3395 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotA | Current motor current [A] | Real |  | HoldingRegister | 3835 | A | Heat Pump cPCO variable
3396 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotV | Current motor voltage [V] | UInt |  | HoldingRegister | 3837 | V | Heat Pump cPCO variable
3397 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_MotPwr | Current motor consumption [W] | Real |  | HoldingRegister | 3839 |  | Heat Pump cPCO variable
3398 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR113_DCBusVoltage | DC bus voltage | UInt |  | HoldingRegister | 3841 |  | Heat Pump cPCO variable
3399 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR134_DCBusRipple | DC bus ripple | UInt |  | HoldingRegister | 3843 |  | Heat Pump cPCO variable
3400 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_DriveTemp | Drive temperature | Real |  | HoldingRegister | 3845 | °C | Heat Pump cPCO variable
3401 | N_Alarm |  | Int |  | HoldingRegister | 4001 |  | Remote alarm management
3402 | AL_ActiveAlarmsQuantity |  | DInt |  | HoldingRegister | 4002 |  | Remote alarm management
3403 | AL_ActiveAlarmsPointer |  | DInt |  | HoldingRegister | 4004 |  | Remote alarm management
3404 | AL_ActiveAlarmsPointerSent |  | DInt |  | HoldingRegister | 4006 |  | Remote alarm management
3405 | AL_ActiveAlarmsNumberSent |  | DInt |  | HoldingRegister | 4008 |  | Remote alarm management
3406 | AL_ActiveAlarmsTimeStampSent |  | DInt |  | HoldingRegister | 4010 |  | Remote alarm management
3407 | AL_LogAlarmsPointer |  | DInt |  | HoldingRegister | 4012 |  | Remote alarm management
3408 | AL_LogAlarmsPointerSent |  | DInt |  | HoldingRegister | 4014 |  | Remote alarm management
3409 | AL_LogAlarmsNumberSent |  | DInt |  | HoldingRegister | 4016 |  | Remote alarm management
3410 | AL_LogAlarmsTypeSent |  | USInt |  | HoldingRegister | 4018 |  | Remote alarm management
3411 | AL_LogAlarmsTimeStampSent |  | DInt |  | HoldingRegister | 4019 |  | Remote alarm management
3412 | Al_SupFan_01 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4021 |  | Fan alarm Register - see BitStruct sheet
3413 | Al_SupFan_02 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4023 |  | Fan alarm Register - see BitStruct sheet
3414 | Al_SupFan_03 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4025 |  | Fan alarm Register - see BitStruct sheet
3415 | Al_SupFan_04 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4027 |  | Fan alarm Register - see BitStruct sheet
3416 | Al_SupFan_05 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4029 |  | Fan alarm Register - see BitStruct sheet
3417 | Al_SupFan_06 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4031 |  | Fan alarm Register - see BitStruct sheet
3418 | Al_SupFan_07 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4033 |  | Fan alarm Register - see BitStruct sheet
3419 | Al_SupFan_08 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4035 |  | Fan alarm Register - see BitStruct sheet
3420 | Al_SupFan_09 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4037 |  | Fan alarm Register - see BitStruct sheet
3421 | Al_SupFan_10 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4039 |  | Fan alarm Register - see BitStruct sheet
3422 | Al_SupFan_11 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4041 |  | Fan alarm Register - see BitStruct sheet
3423 | Al_SupFan_12 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4043 |  | Fan alarm Register - see BitStruct sheet
3424 | Al_SupFan_13 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4045 |  | Fan alarm Register - see BitStruct sheet
3425 | Al_SupFan_14 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4047 |  | Fan alarm Register - see BitStruct sheet
3426 | Al_SupFan_15 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4049 |  | Fan alarm Register - see BitStruct sheet
3427 | Al_ExhFan_01 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4051 |  | Fan alarm Register - see BitStruct sheet
3428 | Al_ExhFan_02 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4053 |  | Fan alarm Register - see BitStruct sheet
3429 | Al_ExhFan_03 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4055 |  | Fan alarm Register - see BitStruct sheet
3430 | Al_ExhFan_04 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4057 |  | Fan alarm Register - see BitStruct sheet
3431 | Al_ExhFan_05 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4059 |  | Fan alarm Register - see BitStruct sheet
3432 | Al_ExhFan_06 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4061 |  | Fan alarm Register - see BitStruct sheet
3433 | Al_ExhFan_07 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4063 |  | Fan alarm Register - see BitStruct sheet
3434 | Al_ExhFan_08 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4065 |  | Fan alarm Register - see BitStruct sheet
3435 | Al_ExhFan_09 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4067 |  | Fan alarm Register - see BitStruct sheet
3436 | Al_ExhFan_10 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4069 |  | Fan alarm Register - see BitStruct sheet
3437 | Al_ExhFan_11 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4071 |  | Fan alarm Register - see BitStruct sheet
3438 | Al_ExhFan_12 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4073 |  | Fan alarm Register - see BitStruct sheet
3439 | Al_ExhFan_13 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4075 |  | Fan alarm Register - see BitStruct sheet
3440 | Al_ExhFan_14 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4077 |  | Fan alarm Register - see BitStruct sheet
3441 | Al_ExhFan_15 | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | DInt |  | HoldingRegister | 4079 |  | Fan alarm Register - see BitStruct sheet
3442 | Al_EC_SupFan_01 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4081 |  | Fan alarm Register - see BitStruct sheet
3443 | Al_EC_SupFan_02 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4082 |  | Fan alarm Register - see BitStruct sheet
3444 | Al_EC_SupFan_03 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4083 |  | Fan alarm Register - see BitStruct sheet
3445 | Al_EC_SupFan_04 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4084 |  | Fan alarm Register - see BitStruct sheet
3446 | Al_EC_SupFan_05 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4085 |  | Fan alarm Register - see BitStruct sheet
3447 | Al_EC_SupFan_06 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4086 |  | Fan alarm Register - see BitStruct sheet
3448 | Al_EC_SupFan_07 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4087 |  | Fan alarm Register - see BitStruct sheet
3449 | Al_EC_SupFan_08 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4088 |  | Fan alarm Register - see BitStruct sheet
3450 | Al_EC_SupFan_09 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4089 |  | Fan alarm Register - see BitStruct sheet
3451 | Al_EC_SupFan_10 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4090 |  | Fan alarm Register - see BitStruct sheet
3452 | Al_EC_SupFan_11 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4091 |  | Fan alarm Register - see BitStruct sheet
3453 | Al_EC_SupFan_12 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4092 |  | Fan alarm Register - see BitStruct sheet
3454 | Al_EC_SupFan_13 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4093 |  | Fan alarm Register - see BitStruct sheet
3455 | Al_EC_SupFan_14 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4094 |  | Fan alarm Register - see BitStruct sheet
3456 | Al_EC_SupFan_15 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4095 |  | Fan alarm Register - see BitStruct sheet
3457 | Al_EC_ExhFan_01 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4096 |  | Fan alarm Register - see BitStruct sheet
3458 | Al_EC_ExhFan_02 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4097 |  | Fan alarm Register - see BitStruct sheet
3459 | Al_EC_ExhFan_03 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4098 |  | Fan alarm Register - see BitStruct sheet
3460 | Al_EC_ExhFan_04 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4099 |  | Fan alarm Register - see BitStruct sheet
3461 | Al_EC_ExhFan_05 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4100 |  | Fan alarm Register - see BitStruct sheet
3462 | Al_EC_ExhFan_06 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4101 |  | Fan alarm Register - see BitStruct sheet
3463 | Al_EC_ExhFan_07 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4102 |  | Fan alarm Register - see BitStruct sheet
3464 | Al_EC_ExhFan_08 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4103 |  | Fan alarm Register - see BitStruct sheet
3465 | Al_EC_ExhFan_09 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4104 |  | Fan alarm Register - see BitStruct sheet
3466 | Al_EC_ExhFan_10 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4105 |  | Fan alarm Register - see BitStruct sheet
3467 | Al_EC_ExhFan_11 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4106 |  | Fan alarm Register - see BitStruct sheet
3468 | Al_EC_ExhFan_12 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4107 |  | Fan alarm Register - see BitStruct sheet
3469 | Al_EC_ExhFan_13 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4108 |  | Fan alarm Register - see BitStruct sheet
3470 | Al_EC_ExhFan_14 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4109 |  | Fan alarm Register - see BitStruct sheet
3471 | Al_EC_ExhFan_15 | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4110 |  | Fan alarm Register - see BitStruct sheet
3472 | Al_Rotary | BitStruct1: VFD Exhaust/Supply Fan # Bit Structure | Dint |  | HoldingRegister | 4111 |  | Fan alarm Register - see BitStruct sheet
3473 | Al_EC_Rotary | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure | Int |  | HoldingRegister | 4113 |  | Fan alarm Register - see BitStruct sheet
4167 | Bldc_Evd_PowerPlus_BLDC1toEVDEVO_RegSubTyp | EVD regulation subtype | Int |  | HoldingRegister | 4114 |  | Heat Pump cPCO variable
4168 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempAlrmThrsh | Discharge gas limit temperature (SIAM Scroll only: for Zone 1b) | Real |  | HoldingRegister | 4115 | °C | Heat Pump cPCO variable
4169 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempAlrmThrshZone1a | Discharge gas limit temperature for Zone 1a (SIAM Scroll only) | Real |  | HoldingRegister | 4117 | °C | Heat Pump cPCO variable
4170 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempCtrlThrsh | Discharge gas temperature control threshold (SIAM scroll only: for zone 1b) | Real |  | HoldingRegister | 4119 | °C | Heat Pump cPCO variable
4171 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempCtrlThrshZone1a | Discharge gas temperature control threshold for Zone 1a (SIAM scroll only) | Real |  | HoldingRegister | 4121 | °C | Heat Pump cPCO variable
4172 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempLimDistance | Action distance from High Temperature limit (to reduce speed rate) | Real |  | HoldingRegister | 4123 | °C | Heat Pump cPCO variable
4173 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempPause | Pause between speed reductions when discharge temp. is over control limit | Int |  | HoldingRegister | 4125 |  | Heat Pump cPCO variable
4174 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_DscgTempSpeedReduction | Speed Reduction %age when discharge temp is over control limit | Real |  | HoldingRegister | 4126 |  | Heat Pump cPCO variable
4175 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_EnvOutMaxT | Out of envelop alarm delay time | Int |  | HoldingRegister | 4128 |  | Heat Pump cPCO variable
4176 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_LowDeltaPAlrmDelay | Low Delta P alarm delay | Int |  | HoldingRegister | 4129 | sec. | Heat Pump cPCO variable
4177 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_MaxSpeedZone1c | Max Speed in rps for Zone 1c (SIAM Scroll) N.B.: integer rps! | Int |  | HoldingRegister | 4130 |  | Heat Pump cPCO variable
4178 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_CstmEnv_SuctTSaturationThrshZone1b1c | Suction sat.temp. threshold from zone 1b (Max120rps) to zone 1c (Max90rps SIAM only) | Real |  | HoldingRegister | 4131 |  | Heat Pump cPCO variable
4179 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DscgSHSetP | SetPoint of Discharge SH (sent to EVD) | Real |  | HoldingRegister | 4133 | K | Heat Pump cPCO variable
4180 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DscgTempNTCT | Time constant of discharge temp sensor | Real |  | HoldingRegister | 4135 |  | Heat Pump cPCO variable
4181 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DscgTempSetP | SetPoint of Discharge Temp (sent to EVD) | Real |  | HoldingRegister | 4137 | °C | Heat Pump cPCO variable
4182 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DTDLTHyst | Hysteresys for Discharge Limit Temp. regulation deactivation | Real |  | HoldingRegister | 4139 | K | Heat Pump cPCO variable
4183 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DTDLTRegOn | Setpoint offset for Discharge Limit Temp. regulation activation | Real |  | HoldingRegister | 4141 | K | Heat Pump cPCO variable
4184 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DTDscgSHHyst | Hysteresys for Discharge Super Heat regulation deactivation | Real |  | HoldingRegister | 4143 | K | Heat Pump cPCO variable
4185 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_DTDscgSHRegOn | Setpoint offset for Discharge Super Heat regulation activation | Real |  | HoldingRegister | 4145 | K | Heat Pump cPCO variable
4186 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_EvdReg_SubTypeRegMode | Regol. Evd SubType: 0=null; 1=SSH; 2=DSH; 3= DLT | Int |  | HoldingRegister | 4147 |  | Heat Pump cPCO variable
4187 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MaxDescendSpeedRate | Max. decrease speed rate (in regulation) [rps/s] | Real |  | HoldingRegister | 4148 |  | Heat Pump cPCO variable
4188 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MaxRisingSpeedRate | Max. increase speed rate (in regulation) [rps/s] | Real |  | HoldingRegister | 4150 |  | Heat Pump cPCO variable
4189 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MaxSlowdownSpeedRate | Decrease speed rate (to come back inside envelope) [rps/s] | Real |  | HoldingRegister | 4152 |  | Heat Pump cPCO variable
4190 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MaxSpeedRpsCustom | Max speed custom (rps) | Real |  | HoldingRegister | 4154 |  | Heat Pump cPCO variable
4191 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MinSpeedControlled | Min speed permitted to control compressor working conditions inside envelop | Real |  | HoldingRegister | 4156 |  | Heat Pump cPCO variable
4192 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_MinSpeedRpsCustom | Min speed custom (rps) | Real |  | HoldingRegister | 4158 |  | Heat Pump cPCO variable
4193 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_StartUpSpeed | Start up speed | Real |  | HoldingRegister | 4160 |  | Heat Pump cPCO variable
4194 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_Speed_SwitchOffSpeedRate | Decrease max speed rate (= max admitted value, to stop compressor) [rps/s] | Real |  | HoldingRegister | 4162 |  | Heat Pump cPCO variable
4195 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_Attempts | Max Number of starting attempts | Int |  | HoldingRegister | 4164 |  | Heat Pump cPCO variable
4196 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_DeltaPDelay | Delay to check increasing DeltaP to validate compressor started | Int |  | HoldingRegister | 4165 |  | Heat Pump cPCO variable
4197 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_DeltaPVariation | Min. variation of Delta P to considered compressor started [bar] | Real |  | HoldingRegister | 4166 | DeltaDegreesFahrenheit | Heat Pump cPCO variable
4198 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_EVDEqualMaxT | Maximum time of EVD propening to equalize pressure | Int |  | HoldingRegister | 4168 |  | Heat Pump cPCO variable
4199 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_EVDEqualPreopen | Preopening of EVD in case of prestart to equalize pressure | Int |  | HoldingRegister | 4169 |  | Heat Pump cPCO variable
4200 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_MaxDeltaP | Max. permitted Delta P to start up [bar] | Real |  | HoldingRegister | 4170 | Bars | Heat Pump cPCO variable
4201 | Bldc_Evd_PowerPlus_CfgEnvCtrl_BLDC1_StartUp_RestartDelay | Restart delay after a start failure | Int |  | HoldingRegister | 4172 |  | Heat Pump cPCO variable
4202 | Bldc_Evd_PowerPlus_Comp_BLDC_1_StLogic_1_EnvZone_1_DistYD | Distance to bottom border line long Y axis | Int |  | HoldingRegister | 4173 |  | Heat Pump cPCO variable
4203 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_CrankCaseHeaterMode | Crank-case heater mode (0=Strategy mng; 1=forcedON; 2=forcedOFF) | Int |  | HoldingRegister | 4174 |  | Heat Pump cPCO variable
4204 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR00_MotCtrlMode | Motor control mode | Int |  | HoldingRegister | 4175 |  | Heat Pump cPCO variable
4205 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR01_MotBaseFreq | Motor base frequency | Real |  | HoldingRegister | 4176 | Hz | Heat Pump cPCO variable
4206 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR02_MotBaseV | Motor base voltage | Int |  | HoldingRegister | 4178 | V | Heat Pump cPCO variable
4207 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR03_MotRatedA | Motor rated current | Real |  | HoldingRegister | 4179 | A | Heat Pump cPCO variable
4208 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR04_MotPwrFactor | Motor power factor | Int |  | HoldingRegister | 4181 |  | Heat Pump cPCO variable
4209 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR05_MaxOutCurrent | Max output current | Real |  | HoldingRegister | 4182 | % | Heat Pump cPCO variable
4210 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR06_MaxOutFreq | Max output frequency | Real |  | HoldingRegister | 4184 | Hz | Heat Pump cPCO variable
4211 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR07_MinOutFreq | Min output frequency | Real |  | HoldingRegister | 4186 | Hz | Heat Pump cPCO variable
4212 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR08_EnRevSpeed | Reverse speed enable | Int |  | HoldingRegister | 4188 |  | Heat Pump cPCO variable
4213 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR09_SpeedDeratingMode | Speed derating mode | Int |  | HoldingRegister | 4189 | °C | Heat Pump cPCO variable
4214 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR10_SkipFreqSetP | Skip frequency: set 1 | Real |  | HoldingRegister | 4190 | Hz | Heat Pump cPCO variable
4215 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR11_SkipFreqBand | Skip frequency: band 1 | Real |  | HoldingRegister | 4192 | Hz | Heat Pump cPCO variable
4216 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR12_SpeedProfileFreq1 | Speed profile: frequency 1 | Real |  | HoldingRegister | 4194 | Hz | Heat Pump cPCO variable
4217 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR13_SpeedProfileFreq2 | Speed profile: frequency 2 | Real |  | HoldingRegister | 4196 | Hz | Heat Pump cPCO variable
4218 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR14_SpeedProfileFreq3 | Speed profile: frequency 3 | Real |  | HoldingRegister | 4198 | Hz | Heat Pump cPCO variable
4219 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR15_SpeedProfileAcceleration1 | Speed profile: acceleration 1 [Hz/s] | Real |  | HoldingRegister | 4200 |  | Heat Pump cPCO variable
4220 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR16_SpeedProfileAcceleration2 | Speed profile: acceleration 2 [Hz/s] | Real |  | HoldingRegister | 4202 |  | Heat Pump cPCO variable
4221 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR17_SpeedProfileAcceleration3 | Speed profile: acceleration 3 [Hz/s] | Real |  | HoldingRegister | 4204 |  | Heat Pump cPCO variable
4222 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR18_SpeedProfileAcceleration4 | Speed profile: acceleration 4 [Hz/s] | Real |  | HoldingRegister | 4206 |  | Heat Pump cPCO variable
4223 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR19_SpeedProfileDelay1 | Speed profile: delay 1 | Int |  | HoldingRegister | 4208 | sec. | Heat Pump cPCO variable
4224 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR20_SpeedProfileDelay2 | Speed profile: delay 2 | Int |  | HoldingRegister | 4209 | sec. | Heat Pump cPCO variable
4225 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR21_SpeedProfileDelay3 | Speed profile: delay 3 | Int |  | HoldingRegister | 4210 | sec. | Heat Pump cPCO variable
4226 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR23_SpeedProfileDeceleration | Speed profile: deceleration [Hz/s] | Real |  | HoldingRegister | 4211 |  | Heat Pump cPCO variable
4227 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR24_SwitchingFreq | Switching frequency | Int |  | HoldingRegister | 4213 |  | Heat Pump cPCO variable
4228 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR25_SwitchingFreqDerating | Switching frequency derating | Int |  | HoldingRegister | 4214 |  | Heat Pump cPCO variable
4229 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR26_RelayCfg | Relay configuration | Int |  | HoldingRegister | 4215 |  | Heat Pump cPCO variable
4230 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR27_MotOvTempAlrmPTC_En | Motor overtemperature alarm (PTC) enable | Int |  | HoldingRegister | 4216 |  | Heat Pump cPCO variable
4231 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR28_MotOvTempAlrmPTC_Delay | Motor overtemperature alarm delay | Int |  | HoldingRegister | 4217 | sec. | Heat Pump cPCO variable
4232 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR29_DataCommTimeout | Data communication fault timeout | Int |  | HoldingRegister | 4218 | sec. | Heat Pump cPCO variable
4233 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR33_StopMode | Stop mode | Int |  | HoldingRegister | 4219 |  | Heat Pump cPCO variable
4234 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR34_FlyingRestart | Flying restart | Int |  | HoldingRegister | 4220 |  | Heat Pump cPCO variable
4235 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR35_V_F_BoostV | V/f boost voltage | Real |  | HoldingRegister | 4221 | % | Heat Pump cPCO variable
4236 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR36_V_F_FreqAdj | V/f frequency adjustment | Real |  | HoldingRegister | 4223 | % | Heat Pump cPCO variable
4237 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR37_V_F_VAdj | V/f voltage adjustment | Real |  | HoldingRegister | 4225 | % | Heat Pump cPCO variable
4238 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR45_MotMagnetizingCurrent | Motor magnetizing current | Real |  | HoldingRegister | 4227 | A | Heat Pump cPCO variable
4239 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR46_StatorResistance | Stator resistance [mohm] | Int |  | HoldingRegister | 4229 |  | Heat Pump cPCO variable
4240 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR47_RotorResistance | Rotor resistance [mohm] | Int |  | HoldingRegister | 4230 |  | Heat Pump cPCO variable
4241 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR48_StatorInductanceLd | Stator inductance Ld [mH] | Real |  | HoldingRegister | 4231 |  | Heat Pump cPCO variable
4242 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR49_LeakageFactor | Leakage factor | Int |  | HoldingRegister | 4233 |  | Heat Pump cPCO variable
4243 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR50_LqInductance | Stator inductance Lq [mH] | Real |  | HoldingRegister | 4234 |  | Heat Pump cPCO variable
4244 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR51_MagnetizingTime | Magnetizing time | Int |  | HoldingRegister | 4236 | msec. | Heat Pump cPCO variable
4245 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR55_SpeedLoopKp | Speed loop Kp | Real |  | HoldingRegister | 4237 | % | Heat Pump cPCO variable
4246 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR56_SpeedLoopTi | Speed loop Ti | Int |  | HoldingRegister | 4239 | msec. | Heat Pump cPCO variable
4247 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR57_StartingCurrent | Starting current | Real |  | HoldingRegister | 4240 | % | Heat Pump cPCO variable
4248 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR58_StartingAFreq | Frequency for starting current | Real |  | HoldingRegister | 4242 | % | Heat Pump cPCO variable
4249 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR65_CrankCaseHeaterCurrent | Crank-case heater current | Real |  | HoldingRegister | 4244 | % | Heat Pump cPCO variable
4250 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR66_STOResetStrategy | Safety torque off alarm autoreset on drive stand-by | Int |  | HoldingRegister | 4246 | % | Heat Pump cPCO variable
4251 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR67_SkipFreqSetP_2 | Skip frequency setpoint 2 | Real |  | HoldingRegister | 4247 | Hz | Heat Pump cPCO variable
4252 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR68_SkipFreqBand_2 | Skip frequency band 2 | Real |  | HoldingRegister | 4249 | Hz | Heat Pump cPCO variable
4253 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR69_SkipFreqSetp_3 | Skip frequency setpoint 3 | Real |  | HoldingRegister | 4251 | Hz | Heat Pump cPCO variable
4254 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR70_SkipFreqBand_3 | Skip frequency band 3 | Real |  | HoldingRegister | 4253 | Hz | Heat Pump cPCO variable
4255 | Bldc_Evd_PowerPlus_CurrCompCfg_PWRP_1_HR77_InductSaturFactor | Inductance saturation factor | Real |  | HoldingRegister | 4255 | % | Heat Pump cPCO variable
4256 | Bldc_Evd_PowerPlus_EVDEVOtoBLDC1_DscgTemp | Discharge temperature | Real |  | HoldingRegister | 4257 | °C | Heat Pump cPCO variable
4257 | Bldc_Evd_PowerPlus_Info_BLDC1_Dbg_FBVersion_Beta | Debug: FB version beta | Int |  | HoldingRegister | 4259 |  | Heat Pump cPCO variable
4258 | Bldc_Evd_PowerPlus_Info_BLDC1_Dbg_FBVersion_X | Debug: FB version x | Int |  | HoldingRegister | 4260 |  | Heat Pump cPCO variable
4259 | Bldc_Evd_PowerPlus_Info_BLDC1_Dbg_FBVersion_Y | Debug: FB version y | Int |  | HoldingRegister | 4261 |  | Heat Pump cPCO variable
4260 | Bldc_Evd_PowerPlus_Info_BLDC1_Dbg_FBVersion_Z | Debug: FB version z | Int |  | HoldingRegister | 4262 |  | Heat Pump cPCO variable
4261 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_ActiveDscgHTLim | Show active value of discharge temp. alarm limit (depending on working zone) | Real |  | HoldingRegister | 4263 | °C | Heat Pump cPCO variable
4262 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_CompRequest | Compressor power request [%] | Real |  | HoldingRegister | 4265 |  | Heat Pump cPCO variable
4263 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_DscgSH | Current discharge superheat | Real |  | HoldingRegister | 4267 | K | Heat Pump cPCO variable
4264 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_DscgTemp | Current discharge temperature | Real |  | HoldingRegister | 4269 | °C | Heat Pump cPCO variable
4265 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_EnvZone | Current envelope zone | Int |  | HoldingRegister | 4271 |  | Heat Pump cPCO variable
4266 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_HTZone | High discharge temperature zone 1a | Int |  | HoldingRegister | 4272 |  | Heat Pump cPCO variable
4267 | Bldc_Evd_PowerPlus_Info_BLDC1_Info_ReqSpeedToPWRP | Required speed to PowerPlus [%] | Real |  | HoldingRegister | 4273 |  | Heat Pump cPCO variable
4268 | Bldc_Evd_PowerPlus_Info_BLDC1_Press_DeltaP | Current delta pressure | Real |  | HoldingRegister | 4275 | Bars | Heat Pump cPCO variable
4269 | Bldc_Evd_PowerPlus_Info_BLDC1_Press_DscgP_Bar | Discharge pressure relative [bar] | Real |  | HoldingRegister | 4277 | Bars | Heat Pump cPCO variable
4270 | Bldc_Evd_PowerPlus_Info_BLDC1_Press_RatioP | Current pressure ratio | Real |  | HoldingRegister | 4279 |  | Heat Pump cPCO variable
4271 | Bldc_Evd_PowerPlus_Info_BLDC1_Press_SuctP_Bar | Suction pressure relative [bar] | Real |  | HoldingRegister | 4281 | Bars | Heat Pump cPCO variable
4272 | Bldc_Evd_PowerPlus_Info_BLDC1_Time_CntDwnDeltaPAlrm | Low pressure difference alarm timing countdown | Int |  | HoldingRegister | 4283 |  | Heat Pump cPCO variable
4273 | Bldc_Evd_PowerPlus_Info_BLDC1_Time_CntDwnOutEnv | Out of envelop timing countdown | Int |  | HoldingRegister | 4284 |  | Heat Pump cPCO variable
4274 | Bldc_Evd_PowerPlus_Info_PWRP1_Dbg_FBVersion_Beta | FB version beta | Int |  | HoldingRegister | 4285 |  | Heat Pump cPCO variable
4275 | Bldc_Evd_PowerPlus_Info_PWRP1_Dbg_FBVersion_X | FB version x | Int |  | HoldingRegister | 4286 |  | Heat Pump cPCO variable
4276 | Bldc_Evd_PowerPlus_Info_PWRP1_Dbg_FBVersion_Y | FB version y | Int |  | HoldingRegister | 4287 |  | Heat Pump cPCO variable
4277 | Bldc_Evd_PowerPlus_Info_PWRP1_Dbg_FBVersion_Z | FB version zzz | Int |  | HoldingRegister | 4288 |  | Heat Pump cPCO variable
4278 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_FreqSetP | Speed reference [Hz/rps] | Real |  | HoldingRegister | 4289 |  | Heat Pump cPCO variable
4279 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_PSD_AAa | Device rated current [AA.a] | Real |  | HoldingRegister | 4291 | A | Heat Pump cPCO variable
4280 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_Hz | Current rotor speed [Hz] | Real |  | HoldingRegister | 4293 | Hz | Heat Pump cPCO variable
4281 | Bldc_Evd_PowerPlus_Info_PWRP1_Info_RotorSpeed_rpm | Current rotorspeed [rpm] | Int |  | HoldingRegister | 4295 | RPM | Heat Pump cPCO variable
4282 | Bldc_Evd_PowerPlus_Info_PWRP1_Mng_MotSelect_AAa | Rated current of compressor | Int |  | HoldingRegister | 4296 | A | Heat Pump cPCO variable
4283 | Bldc_Evd_PowerPlus_Info_PWRP1_UI_RatedCrankCaseHeatA | Rated crankcase heating current | Real |  | HoldingRegister | 4297 | A | Heat Pump cPCO variable
4284 | Bldc_Evd_PowerPlus_Info_PWRP1_UI_RatedInductsatReductA | Inductance saturation reduction (%age at rated current) | Real |  | HoldingRegister | 4299 | % | Heat Pump cPCO variable
4285 | Bldc_Evd_PowerPlus_Info_PWRP1_UI_RatedStartingA | Rated starting current | Real |  | HoldingRegister | 4301 | A | Heat Pump cPCO variable
4286 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR104_DriveStatus | 0: Stop; 1: Run; 2: Alarm; 3: Crankcase heating; 4:DCbus ready) | Int |  | HoldingRegister | 4303 |  | Heat Pump cPCO variable
4287 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR105_AlrmCode | see doc | Int |  | HoldingRegister | 4304 |  | Heat Pump cPCO variable
4288 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR124_OperatingSwitchingFreq | PWM switching frequency (0: 4kHz, 1: 6kHz, 2: 8kHz) | Int |  | HoldingRegister | 4305 |  | Heat Pump cPCO variable
4289 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR125_PreRampOutput_SpeedRef | Pre-ramp output frequency reference | Real |  | HoldingRegister | 4306 |  | Heat Pump cPCO variable
4290 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR141_BootLoaderRelease | Bootloader version | Int |  | HoldingRegister | 4308 |  | Heat Pump cPCO variable
4291 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR142_FirmwareRelease | Firmware version | Int |  | HoldingRegister | 4309 |  | Heat Pump cPCO variable
4292 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR143_FirmwareCRC | Firmware checksum | Int |  | HoldingRegister | 4310 |  | Heat Pump cPCO variable
4293 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR144_MotCtrlRelease | Motor control version | Int |  | HoldingRegister | 4311 |  | Heat Pump cPCO variable
4294 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR149_HardwareIdentification | Hardware identification | Int |  | HoldingRegister | 4312 |  | Heat Pump cPCO variable
4295 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR153_OvldMot_accumulator | Motor Overload Accumulator | Real |  | HoldingRegister | 4313 |  | Heat Pump cPCO variable
4296 | Bldc_Evd_PowerPlus_IRparam_PWRP1_IR154_OvldDrive_accumulator | Drive Overload Accumulator | Real |  | HoldingRegister | 4315 |  | Heat Pump cPCO variable
4297 | Bldc_Evd_PowerPlus_MiscMng_BLDC1_Mng_CompTyp | Compressor model (previous value) | Int |  | HoldingRegister | 4317 |  | Heat Pump cPCO variable
4298 | Bldc_Evd_PowerPlus_MiscMng_BLDC1_Mng_PwrpMotTyp | Compressor model (PowerPlus) | Int |  | HoldingRegister | 4318 |  | Heat Pump cPCO variable
4299 | Bldc_Evd_PowerPlus_MiscMng_PWRP1_Mng_DriveTyp | Drive type | Int |  | HoldingRegister | 4319 |  | Heat Pump cPCO variable
4300 | Bldc_Evd_PowerPlus_MiscMng_PWRP1_Mng_MotPoles | Motor pole pairs | Int |  | HoldingRegister | 4320 |  | Heat Pump cPCO variable
4301 | Bldc_Evd_PowerPlus_MiscMng_PWRP1_Mng_WriteDefault | Write default request | Int |  | HoldingRegister | 4321 |  | Heat Pump cPCO variable
4302 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondAlrmDT_Val | HiTcond (high condensing temperature) alarm timeout | Int |  | HoldingRegister | 4322 | sec. | Heat Pump cPCO variable
4303 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondThrsh_Val | HiTcond (high condensing temperature) threshold | Real |  | HoldingRegister | 4323 | °C | Heat Pump cPCO variable
4304 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondTi_Val | HiTcond (high condensing temperature) integral time | Real |  | HoldingRegister | 4325 | sec. | Heat Pump cPCO variable
4305 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_ModThermDiff_Val | Modulating thermostat: differential | Real |  | HoldingRegister | 4327 | K | Heat Pump cPCO variable
4306 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_ModThermSet_Val | Modulating thermostat: setpoint | Real |  | HoldingRegister | 4329 | °C | Heat Pump cPCO variable
4307 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_AuxRegulation_ModThermSH_Offset_Val | Modulating thermostat: superheat setpoint offset | Real |  | HoldingRegister | 4331 | K | Heat Pump cPCO variable
4308 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Configuration_GasTypAux_Val | Refirenat for auxiliary regulation | Int |  | HoldingRegister | 4333 |  | Heat Pump cPCO variable
4309 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_FastClosMoveRate_Val | EEV: emergency EEV closing speed | Int |  | HoldingRegister | 4334 |  | Heat Pump cPCO variable
4310 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_FullClosSteps_Val | EEV closing steps | Int |  | HoldingRegister | 4335 |  | Heat Pump cPCO variable
4311 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_MoveDuty_Val | EEV duty cycle | Int |  | HoldingRegister | 4336 | % | Heat Pump cPCO variable
4312 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_MoveRate_Val | EEV step rate | Int |  | HoldingRegister | 4337 |  | Heat Pump cPCO variable
4313 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_RegMaxPos_Val | EEV maximum steps | Int |  | HoldingRegister | 4338 |  | Heat Pump cPCO variable
4314 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_EEV_Config_RegMinPos_Val | EEV minimum steps | Int |  | HoldingRegister | 4339 |  | Heat Pump cPCO variable
4315 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_CtrlDirP_Set_Val | EPR pressure setpoint | Real |  | HoldingRegister | 4340 | Bars | Heat Pump cPCO variable
4316 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_CtrlRevP_Set_Val | Hot gas by-pass pressure setpoint | Real |  | HoldingRegister | 4342 | Bars | Heat Pump cPCO variable
4317 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_CtrlRevTempSet_Val | Hot gas by-pass temperature setpoint | Real |  | HoldingRegister | 4344 | °C | Heat Pump cPCO variable
4318 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_LOP_Thrsh_Val | LOP (low evaporation temperaure) threshold | Real |  | HoldingRegister | 4346 | °C | Heat Pump cPCO variable
4319 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_LOP_Ti_Val | LOP (low evaporation temperaure) integral time | Real |  | HoldingRegister | 4348 | sec. | Heat Pump cPCO variable
4320 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_LowSH_Thrsh_Val | LowSH (low superheat) threshold | Real |  | HoldingRegister | 4350 | K | Heat Pump cPCO variable
4321 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_LowSH_Ti_Val | LowSH (low superheat) integral time | Real |  | HoldingRegister | 4352 | sec. | Heat Pump cPCO variable
4322 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_MOP_Thrsh_Val | MOP (high evaporation temperature) threshold | Real |  | HoldingRegister | 4354 | °C | Heat Pump cPCO variable
4323 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_MOP_Ti_Val | MOP (high evaporation temperature) integral time | Real |  | HoldingRegister | 4356 | sec. | Heat Pump cPCO variable
4324 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_PID_Kp_Val | PID proportional gain | Real |  | HoldingRegister | 4358 |  | Heat Pump cPCO variable
4325 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_PID_Td_Val | PID dervative time | Real |  | HoldingRegister | 4360 |  | Heat Pump cPCO variable
4326 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_PID_Ti_Val | PID integral time | Real |  | HoldingRegister | 4362 | sec. | Heat Pump cPCO variable
4327 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_SH_Set_MskLimMax | Superheat setpoint limit max | Real |  | HoldingRegister | 4364 | K | Heat Pump cPCO variable
4328 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_SH_Set_MskLimMin | Superheat setpoint limit min | Real |  | HoldingRegister | 4366 | K | Heat Pump cPCO variable
4329 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_MainRegulation_SH_Set_Val | Superheat setpoint | Real |  | HoldingRegister | 4368 | K | Heat Pump cPCO variable
4330 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_CO2_A_Val | CO2 A coefficient | Real |  | HoldingRegister | 4370 |  | Heat Pump cPCO variable
4331 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_CO2_B_Val | CO2 B coefficient | Real |  | HoldingRegister | 4372 |  | Heat Pump cPCO variable
4332 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_CtrlLiqdSet_Val | Flooded evap./cond. liquid level control set-point | Real |  | HoldingRegister | 4374 |  | Heat Pump cPCO variable
4333 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_GasTyp_Val | Refigerant | Int |  | HoldingRegister | 4376 |  | Heat Pump cPCO variable
4334 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_LOP_AlrmDT_Val | LOP (low evaporation temperaure) alarm timeout | Int |  | HoldingRegister | 4377 | sec. | Heat Pump cPCO variable
4335 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_LowSH_AlrmDT_Val | LowSH (low superheat) alarm timeout | Int |  | HoldingRegister | 4378 | sec. | Heat Pump cPCO variable
4336 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_LowSuctAlrmDT_Val | Low suction temperaure alarm timeout | Int |  | HoldingRegister | 4379 | sec. | Heat Pump cPCO variable
4337 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_LowSuctAlrmThrsh_Val | LOP (low evaporation temperaure) alarm timeout | Real |  | HoldingRegister | 4380 | °C | Heat Pump cPCO variable
4338 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_MOP_AlrmDT_Val | MOP (high evaporation temperature) timeout | Int |  | HoldingRegister | 4382 | sec. | Heat Pump cPCO variable
4339 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_SH_WaitDT_Val | Regulation starting delay | Int |  | HoldingRegister | 4383 | sec. | Heat Pump cPCO variable
4340 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_StandByEEV_OpPos_Val | Standby valve opening position % | Int |  | HoldingRegister | 4384 | % | Heat Pump cPCO variable
4341 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Regulation_StartEEV_OpRatio_Val | Valve nominal opening at start-up (EVAP/EEV capacity ratio) | Int |  | HoldingRegister | 4385 | % | Heat Pump cPCO variable
4342 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_SelfTuning_SelfTuningLastResult_Val | Last tuning result | Int |  | HoldingRegister | 4386 |  | Heat Pump cPCO variable
4343 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_SelfTuning_SelfTuningMethod_Val | Tuning method | Int |  | HoldingRegister | 4387 |  | Heat Pump cPCO variable
4344 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_SelfTuning_SelfTuningStatus_Val | Adaptive regulation status | Int |  | HoldingRegister | 4388 |  | Heat Pump cPCO variable
4345 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CO2_P_Val | CO2 gas cooler outlet pressure | Real |  | HoldingRegister | 4389 | Bars | Heat Pump cPCO variable
4346 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CO2_Set_Val | CO2 gas cooler pressure setpoint | Real |  | HoldingRegister | 4391 | Bars | Heat Pump cPCO variable
4347 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CO2_Temp_Val | CO2 gas cooler outlet temperature | Real |  | HoldingRegister | 4393 | °C | Heat Pump cPCO variable
4348 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CtrlDirP_P_Val | EPR Pressure (back pressure) | Real |  | HoldingRegister | 4395 | Bars | Heat Pump cPCO variable
4349 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CtrlLiqdLev_Val | Flooded evap./cond. liquid level control % | Real |  | HoldingRegister | 4397 |  | Heat Pump cPCO variable
4350 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CtrlRevP_P_Val | Hot gas by-pass pressure | Real |  | HoldingRegister | 4399 | Bars | Heat Pump cPCO variable
4351 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_CtrlRevTempTemp_Val | Hot gas by-pass temperature | Real |  | HoldingRegister | 4401 | °C | Heat Pump cPCO variable
4352 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_ModThermTemp_Val | Modulatin thermostat temperature | Real |  | HoldingRegister | 4403 | °C | Heat Pump cPCO variable
4353 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SbC_BubTemp_Val | Condensing bubble termperature for Subcooling measure | Real |  | HoldingRegister | 4405 | °C | Heat Pump cPCO variable
4354 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SbC_CondP_Val | Condensing pressure for Subcooling measure | Real |  | HoldingRegister | 4407 | Bars | Heat Pump cPCO variable
4355 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SbC_LiqdTemp_Val | Condensing liquid termperature for Subcooling measure | Real |  | HoldingRegister | 4409 | °C | Heat Pump cPCO variable
4356 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_EVD_Variables_SbC_Val | Subcooling | Real |  | HoldingRegister | 4411 | K | Heat Pump cPCO variable
4357 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Inputs_S1_Val | Probe S1 value | Real |  | HoldingRegister | 4413 | Bars | Heat Pump cPCO variable
4358 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Inputs_S2_Val | Probe S2 value | Real |  | HoldingRegister | 4415 | °C | Heat Pump cPCO variable
4359 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Inputs_S3_Val | Probe S3 value | Real |  | HoldingRegister | 4417 | Bars | Heat Pump cPCO variable
4360 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Inputs_S4_Val | Probe S4 value | Real |  | HoldingRegister | 4419 | °C | Heat Pump cPCO variable
4361 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Superparameters_AuxRegulationCom_Val | Auxiliary regulation | Int |  | HoldingRegister | 4421 |  | Heat Pump cPCO variable
4362 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Superparameters_EEVtype_Val | Valve | Int |  | HoldingRegister | 4422 |  | Heat Pump cPCO variable
4363 | Bldc_Evd_PowerPlus_Params_EVDEMB_1_Superparameters_MainRegulation_Val | Main regulation | Int |  | HoldingRegister | 4423 |  | Heat Pump cPCO variable
4364 | Comp1_BLDC_DevPwr | Power | Real |  | HoldingRegister | 4424 |  | Heat Pump cPCO variable
4365 | Comp1_BLDC_OnThrsh | Threshold [rps] to switch on the BLDC | Real |  | HoldingRegister | 4426 |  | Heat Pump cPCO variable
3982 | MB_Devices.SerDevCfg_THTN_1.DevAddr |  | UDINT |  | HoldingRegister | 4500
3983 | HMI_MB_Address |  | UDINT |  | HoldingRegister | 4502
3984 | Modbus_Set.Opoz100ms |  | Dint |  | HoldingRegister | 4504
3985 | VFD_SupSet_RPM |  | Real |  | HoldingRegister | 4506 | RPM
3986 | VFD_Max_RPM |  | Int |  | HoldingRegister | 4508 | RPM
3987 | VFD_RetSet_RPM |  | Real |  | HoldingRegister | 4509 | RPM
3988 | VFD_Max_RPM_2 |  | Int |  | HoldingRegister | 4511 | RPM
3989 | PwdUser |  | UInt |  | HoldingRegister | 4512
3990 | PwdService |  | UInt |  | HoldingRegister | 4513
3991 | PwdManuf |  | UInt |  | HoldingRegister | 4514
3992 | MB_Set_Password |  | Int |  | HoldingRegister | 4515
3993 | Pressure3_Simulation_Var |  | Int |  | HoldingRegister | 4516 | Pa
3994 | Pressure4_Simulation_Var |  | Int |  | HoldingRegister | 4517 | Pa
3995 | Pressure5_Simulation_Var |  | Int |  | HoldingRegister | 4518 | Pa
3996 | Pressure1_Simulation_Var |  | Int |  | HoldingRegister | 4519 | Pa
3997 | Pressure2_Simulation_Var |  | Int |  | HoldingRegister | 4520 | Pa
3998 | SupHum_Simulation_Var |  | Real |  | HoldingRegister | 4521 | %
3999 | RetHum_Simulation_Var |  | Real |  | HoldingRegister | 4523 | %
4000 | ReadConfigFile.pGDFileReadStatus |  | USINT |  | HoldingRegister | 4525
2412 | AHU_ID_Char[0] | ASCII code for AHU ID character | Int | Read | InputRegister | 2001
2413 | AHU_ID_Char[1] | ASCII code for AHU ID character | Int | Read | InputRegister | 2002
2414 | AHU_ID_Char[2] | ASCII code for AHU ID character | Int | Read | InputRegister | 2003
2415 | AHU_ID_Char[3] | ASCII code for AHU ID character | Int | Read | InputRegister | 2004
2416 | AHU_ID_Char[4] | ASCII code for AHU ID character | Int | Read | InputRegister | 2005
2417 | AHU_ID_Char[5] | ASCII code for AHU ID character | Int | Read | InputRegister | 2006
2418 | AHU_ID_Char[6] | ASCII code for AHU ID character | Int | Read | InputRegister | 2007
2419 | AHU_ID_Char[7] | ASCII code for AHU ID character | Int | Read | InputRegister | 2008
2420 | AHU_ID_Char[8] | ASCII code for AHU ID character | Int | Read | InputRegister | 2009
2421 | AHU_ID_Char[9] | ASCII code for AHU ID character | Int | Read | InputRegister | 2010
2422 | AHU_ID_Char[10] | ASCII code for AHU ID character | Int | Read | InputRegister | 2011
2423 | AHU_ID_Char[11] | ASCII code for AHU ID character | Int | Read | InputRegister | 2012
2424 | AHU_ID_Char[12] | ASCII code for AHU ID character | Int | Read | InputRegister | 2013
2425 | AHU_ID_Char[13] | ASCII code for AHU ID character | Int | Read | InputRegister | 2014
2426 | AHU_ID_Char[14] | ASCII code for AHU ID character | Int | Read | InputRegister | 2015
2427 | AHU_ID_Char[15] | ASCII code for AHU ID character | Int | Read | InputRegister | 2016
2428 | AHU_ID_Char[16] | ASCII code for AHU ID character | Int | Read | InputRegister | 2017
2429 | AHU_ID_Char[17] | ASCII code for AHU ID character | Int | Read | InputRegister | 2018
2430 | AHU_ID_Char[18] | ASCII code for AHU ID character | Int | Read | InputRegister | 2019
2431 | AHU_ID_Char[19] | ASCII code for AHU ID character | Int | Read | InputRegister | 2020
2442 | CurrVer.X | SYS - System - Application Version - X . _ . _ _ _ _ _ _ | UInt | Read | InputRegister | 2031
2443 | CurrVer.Y | SYS - System - Application Version - _ . Y . _ _ _ _ _ _ | UInt | Read | InputRegister | 2032
2444 | CurrVer.Z | SYS - System - Application Version - _ . _ . Z Z Z _ _ _ | UInt | Read | InputRegister | 2033
2445 | CurrVer.D | SYS - System - Application Version - _ . _ . _ _ _ _ D D | UInt | Read | InputRegister | 2034
3878 | SupplyVoltage[1] |  | Udint | Read | InputRegister | 2035 |  | 0 - Unknown 1 - AC 2 - DC 3 - AC Fail 4 - DC Fail
3879 | SupplyVoltageType[2] |  | Udint | Read | InputRegister | 2037

## BitStruct
BitStruct1: VFD Exhaust/Supply Fan # Bit Structure |  |  | BitStruct2: EC Ehxaust/Supply Fan # Bit Structure
Register | Bit | Description | Register | Bit | Description
REG1 | 0 | Communication Error | REG1 | 0 | Circuit Fault
| 1 | Hardware Fault |  | 1 | Hot
| 2 | Cut Off |  | 2 | I2RIGBT Fault
| 3 | DC Overload |  | 3 | IGBTOvercurrent
| 4 | Electric Thermal |  | 4 | Motor Fault
| 5 | External Fault A |  | 5 | Overvoltage
| 6 | External Fault B |  | 6 | ParametersCRC
| 7 | Ground Fault |  | 7 | Phase Loss
| 8 | HeatSink |  | 8 | Too Hot
| 9 | Offline |  | 9 | Heat Sink
| 10 | Option |  | 10 | Undervoltage
| 11 | Parameters Error |  | 12
| 12 |  |  | 13
| 13 |  |  | 14
| 14 |  |  | 15
15
REG2 | 0 | Inverter OverHeat
| 1 | Cooling Fan Fault
| 2 | Motor OverHeat
| 3 | OverCurrent
| 4 | Low Voltage
| 5 | OverVoltage
| 6 | OverLoad
| 7 | PhaseLost
| 8 | PhaseOpen
9
10
11
12
13
14
15